| مشروع اعادة تأهيل مشتل الشوبك المواصفات الفنيـة مجموع صفحات هذا المجلد 294 صفحة شاملة صفحة الغلاف |  |
| --- | --- |

المحتويات:

البنــــد					رقم الصفحة

المواصفـات الفنيـة العامـة:	3

المواصفـات  الفنيـة الخاصـة	4

1.	شروط عامة	4

2.	أعمال الحفريات والردميات والطمم	5

3.	أعمال الخرسانـة وحديد التسليح:	6

4.	أعمال الطوب	8

5.	أعمال القصارة	10

6.	أعمال البلاط والرخام والأرضيات	11

7.	أعمال المنجور	11

8.	الأعمال  المعدنية والالومنيوم  والـ P.V.C:	12

9.	أعمال  الطراشة والدهان:	13

10.	أعمال العزل على السطوح:	15

11.	الأعمال الخارجية:	15

12.	المواصفات و الشروط الخاصة بالاعمال الكهربائية:	17

13.	الاعمال الميكانيكية:	87

14. المواصفات الفنية لأثاث المختبرات	284

- المواصفـات الفنيـة العامـة:

- المواصفات الفنية العامة للمباني

الصادرة عن وزارة الأشغال العامة والإسكان لسنة 1996، وما صدر عنها من ملاحق وتعديلات، وتعتبر جزء لا يتجزأ من وثائق العقد، وتعتمد هذه المواصفات كمواصفات عامة للمشروع مع مراعاة ما ورد بالمواصفات الفنية الخاصة حيث تعتبر المواصفات الفنية الخاصة مقدمة على المواصفات الفنية العامة ولها الأولوية في التطبيق، وتشمل المواصفات الفنية العامة المجلدات التالية:

أ- المجلد الأول: الأعمال المدنية والمعمارية للمباني

ب- المجلد الثاني: الخدمات الميكانيكية للمباني

جـ- المجلد الثالث: الخدمات الكهربائية للمباني

- المواصفات القياسية والكودات

تعتمد الكودات والمواصفات القياسية التالية :

أ-  المواصفات القياسية الاردنية الصادرة عن مؤسسة المواصفات والمقاييس بوزارة الصناعة والتجارة حتى تاريخ تقديم العطاء.

ب- كودات دستور البناء الوطني الاردني الصادر عن وزارة الاشغال العامة والإسكان.

ج- الكود العربي لتصميم وتنفيذ المنشات الخرسانية الصادرة عن اتحاد المهندسين العرب سنة 1977 وأية تعديلات أو إضافات أو ملحقات تمت بعد ذلك ويستعمل هذا الكود في تحديد الأحمال والاجهادات ومرجعا لتصميم طرق الإنشاء وتحديد خواص المواد وتقييم نتائج الخرسانة المنفذة.

د-  قانون البناء الوطني الأردني رقم ( 7 ) لعام 1993 وتعديلاته .

هـ- الكود الأردني الخاص بالمنشآت الفولاذية الصادر عن وزارة الأشغال العامة والإسكان ويعتمد الكود الأمريكي ( ASTM ) لما لم يرد في الكود الأردني.

و- المواصفات القياسية العالمية الواردة ضمن هذه المواصفات.

ويجب أن تكون هذه المراجع في كافة الأحوال آخر إصدار وعلى المقاول تزويد المهندس بنسخ   عن أي من هذه المواصفات أو أي جزء منها عند الحاجة إليها وحسب طلب المهندس.

- المواصفـات  الفنيـة الخاصـة

شروط عامة

تعتبر المواصفات الفنية الخاصة مكملة لجداول الكميات والمواصفات الفنية العامة ومتممه لها ويجب أن تكون الأسعار لكل بند شاملة لما هو مذكور في المواصفات الفنية الخاصة لكل بند إضافة لما هو مذكور في نفس البند.

تعتبر المواصفات الفنية التالية والمذكورة في بنود جداول الكميات جزءا من المواصفات المطلوب تنفيذ الأعمال بموجبها و تعتبر متممه ومتقدمة على المواصفات العامة للأخذ بها وفي حالة وجود تعارض أو عدم وضوح أو التباس بين أي من هذه المواصفات فأن تحديد المواصفة المطلوبة في هذه الحالة من صلاحية المهندس ويكون قراره نهائيا.

سواء ذكر في جدول الكميات أو لم يذكر جملة وحسب المواصفات، فإنه من المؤكد أن المطلوب تنفيذه هو حسب المواصفات الفنية الخاصة والعامة للمشروع، مع إعطاء الأولوية للتطبيق للمواصفات الفنية الخاصة وأنها تكمل جداول الكميات.

عند ورود كلمة " كالبند السابق " أو " كالبند رقم ... " فإن هذا يعني أن أسعار ومواصفات البند المعني تشمل كافة ما يشمله البند المشار إليه، مع الأخذ بعين الاعتبار أية إضافة أو إلغاء يتم تحديدها ضمن نفس البند المعني والمواصفات الفنية الخاصة له.

البنود التي لا يوجد لها تفاصيل معمارية بالمخططات يتم تسعيرها حسب الوصف الوارد في نص البند بالإضافة إلى المواصفات الفنية الخاصة لهذا البند ومن خلال المخططات التي تشير إلى هذا العمل أو توضحه.

أعمال الحفريات والردميات والطمم

أعمال الحفريات: تشمل أسعار أعمال الحفريات ما يلي:

إخلاء الموقع مـن كافـة الأنقاض والنفايات قبل مباشرة العمل وكسر وإزالة أي من الأساسات أو المجاري القديمة وأي من العوائق الأخرى .

تنظيف الموقع من الشجيرات واستئصال جميع جذورها وبحسب رأي المهندس.

الحفر بأي تربة مهما كان نوعها بما في ذلك الصخرية منها ( ما لم يذكر خلاف ذلك صراحة ) .

الحفر لأي عمق ( ما لم يذكر خلاف ذلك صراحة ) .

البدء بالحفريات على أي منسوب كان .

إنهاء الحفريات بشكل مستقيم أو مائل أو قوسي حسب المبين على المخططات

زيادة حجم المواد بعد الحفر .

حفظ الحفريات من المياه ونضح المياه التي تتجمع في الحفريات أثناء مراحل العمل.

حماية الأعمال ضد المياه السطحية أينما يتوقع وجودها .

التسوية والدك والتثديب وتدرج الأرضيات وتثديب جوانب وأرضيات الحفريات.

التدفيف والتدعيم.

اخذ الاعتبار لمجالات العمل.

تشوين الصالح من ناتج الحفر لأعمال الطمم .

التصرف بناتج الحفر للطمم ضمـن الموقـع من منتخب ناتج الحفر وتسوية السطوح النهائية لجميع الأرضيات في عدة مراحل حسب تقدم العمل .

نقل المواد الفائضة بعد الطمم إلى خارج الموقع والى الأماكن المصرح بها من قبل المهندس أو الجهات المسؤولة .

كلفة أعمال الطمم ناتج الحفريات لكامل مساحة أرض المشروع وذلك ضمن المباني الخرسانية وتحت الأرضيات والساحات وحول الأساسات والجدران الإستنادية وحيثما يلزم للوصول إلى المناسيب النهائية المبينة على المخططات تكون محملة على أسعار الحفر (ولاتكال ولا يدفع أي علاوة أو سعر إضافي) وعلى المقاول أخذ موافقة المهندس على المواد المختارة لأعمال الطمم سواء كانت من ناتج الحفريات أو من خارج الموقع.

قبل المباشرة بأعمال الحفريات على المقاول تزويد المهندس المشرف بمخطط كنتورى يبين مناسيب الأرض الطبيعية قبل الحفر وضمن فترات لا تتعدى (5)متر لكل فترة وعليه أن يأخذ موافقة المهندس على هذا المخطط.

التحقق من أعماق الحفريات: يقوم المتعهد بالتحقق من قدرة تحمل التربة وملائمتها للأعمال التصميمية حسب المخططات بعد عمل الحفريات وإذا استدعت طبيعة التربة بعد التحقق عن قوة تحملها أي تعديل قد يطرأ على بنود العطاء بزيادة أو نقصان فعليه تنفيذ ذلك ولا يحق له المطالبة بأسعار إضافية وتكال من ضمن أسعار بنود العطاء و تقاس أعمال الحفريات للقواعد والأساسات وخلافه من منسوب الأرض الطبيعية ومنسوب التسوية أيهما أقل ويكون الكيل الهندسي حسب المخططات.

لا تنص هذه المواصفات على وجود مسافة عمل (working space) حول جوانب الحفريات "ولا تكال ولا تدفع أيضا " علاوة أو سعر إضافي عنها.

أعمال الردميات:

شروط القبول للمناطق التي سيتم ردمها:-

بجب أن يكون الدمك للمناطق المردومة كافياً لتصل كل المواد المدموكة إلى كثافة جافة تساوي 95% أو أكثر من الكثافة الجافة القصوى التي يحددها المختبر وذلك عند فحصها باختبار بروكتر المعدل كما في المادة (208/3 ) بما يتعلق بالأماكن ذات الارتباط في المباني وحسب المواصفات القياسية لأعمال الطرق في أماكن الطرق والساحات التي سيتم تزفيتها.

على المقاول أن يقوم وعلى نفقته الخاصة بإجراء الاختبارات المطلوبة لإقناع المهندس بأن أعمال الدمك قد تم تنفيذها طبقا للمواصفات وقد حققت النتائج المطلوبة في الاختبارات.

يتم تحديد النقاط التي سيتم فحصها في أماكن الموقع بما يناسب نوعية العمل الذي تم بها بحسب رأى المهندس.

المواصفات الفنية للطمم من المواد المختارة

التصنيف المجموعي يكون " A2 - 5, A2 - 4, A1 - b, A1 -a  " بمعامل لدونة لا يزيد عن (10).

أن لا يزيد الحجم الأكبر عن 3 "

لتحديد الخصائص عادة تجرى فحوص التدرج الحجمي وحدود ايتربورغ.

المواصفات للطمم ناتج الحفريات: يعتبر ناتج الحفريات صالحاً لأعمال الطمم إذا حقق الخصائص التالية:

أن لا يكون ذو تصنيف مجموعي " A7, A6 "

أن لا تقل الكثافة الجافة العظمى عن 1.6 غم /سم3.

وبناء عليه فإن تحديد الخصائص أعلاه يشمل إجراء تجارب التدرج الحجمي وحدود ايتربورغ إضافة إلى فحص البروكتور.

أما الحدود الدنيا والعليا للمواصفات المتبقية في تحديد التصنيف بناء على نتائج الفحوص المخبرية فيمكن الاستعانة بجدول تصنيف التربة ومجموعات التربة والحصى حسب المواصفات لجمعية مهندسي الطرق الأمريكية "AASHTO "

أعمال الخرسانـة وحديد التسليح:

الإسمنت المستخدم لأعمال العطاء كما يلي:-

لجميع أنواع الخرسانة التي فوق منسوب البلاط أو المدة الأرضية اسمنت بورتلندي .

المقصود بمقاومة الخرسانة أنها مقاومة الكسر بالضغط للمكعبات القياسية بعد 28 يوم من الصب بالكغم/سم2. تشمل جميع الأعمال الواردة في هذا القسم تقديم جميع المواد والمعدات والعمال والنقل إلى الموقع وضمن الموقع .

جميع الخرسانة المستخدمة هي خرسانة جاهزة الصب Ready Mi

تشمل أسعار أعمال الخرسانة المصبوبة وذلك لخرسانة التصفيحة خلف الحجر في الموقع ما يلي:-

خلط الخرسانة حسب المواصفات .

صب الخرسانة ورجها بالرجاجات ودكها حول حديد التسليح وبين القوالب على أن لا تقل دورة الرجاجات عن 7000 ذبذبة / دقيقة.

الإيناع والرش بالماء واللف والتغطية بالخيش المرطب أو اللفائف المانعة لتسرب الماء لجميع عناصر المشروع الإنشائية المختلفة.

العمل في جميع المقاطع والأشكال .

العمل بأي شكل سواء أفقي أم مائل .

العمل في أي موقع في المشروع وعلى أي ارتفاع .

الصب في خانات متعاقبة .

تدريج ودك الخرسانة والتسوية بالمالج .

عمل الفرزات والثقوب والتلسين والنقر والحفر والزوايا المشطوفة وغيرها من أعمال مشابهة في الخرسانة قبل جفافها

النقر والتلسين والحشو بالروبة وبمونة الاسمنت والرمل .

عمل السقالات (الشدات) الخشبية أو المعدنية والطوبار ( القوالب ) ما لم يذكر خلاف ذلك .

تقديم وتركيب المرابط المعدنية لربط أعمال البناء مستقبلا.

أعمال النهو للسطوح المكشوفة .

المخاليط المميعة والمانعة لنش الماء وأي مخاليط مطلوبة .

لا يشمل السعر حديد التسليح ( إلا إذا ذكر خلاف ذلك ).

تقاس الخرسانة صافية ويخصم حجم الطوب المفرغ أو البولسترين وما ماثله من حجم خرسانة العقدات غير أنه لا يتم خصم:

حجم حديد التسليح في الخرسانة.

الفتحات التي لا تزيد عن 0.05 م3.

على المقاول فحص الخلطات الخرسانية بشكل دوري كما يلي:-

لكل 50 متر مكعب خرسانة تؤخذ على الأقل ستة مكعبات ممثلة بحيث تفحص ثلاثة بعد أسبوع والثلاثة الباقية بعد 28 يوم.

لكل يوم صب إذا كان الصب على مراحل متقطعة تؤخذ ستة مكعبات تفحص ثلاثة بعد أسبوع والثلاثة الباقية بعد 28 يوماً.

يشترط أن لا يقل الحد الأدنى لمحتوى الإسمنت /متر مكعب من الخرسانة عن الكمية المطلوبة في المواصفات ووثائق العقد حتى لو حققت الخرسانة القوة المطلوبة بكمية من الإسمنت.

لا يسمح الصب إذا زادت درجة حرارة الخرسانة عند وقت الصب عن 32 درجة مئوية أو قلت عن 4 درجات مئوية، وعلى المقاول اتخاذ كافة التدابير اللازمة للتقيد بذلك، وخلافاً لذلك فإن للمهندس الحق باتخاذ التدابير اللازمة للمحافظة على هذه المواصفة، ويتحمل المقاول أي كلفة مترتبة على هذه التدابير دون أن يكون له حق الاعتراض على ذلك.

على المتعهد ان يقوم بتصميم خلطة خرسانية او تصميم خلطة اسفلتية من مختبر معتمد شاملة لما يلي:-

أن يؤخذ بعين الاعتبار عند التصميم طبيعة العمل وطبيعة اماكن الصب وظروف العمل.

ان يؤخذ بعين الاعتبار عند حساب نسب التصميم اية اضافات على الخلطات في الموقع كالمادة المميعة مثلا وغيرها.

ان يكون التصميم حاويا لفحوصات الخلطة التجريبية وخواص الخرسانة الطازجة.

شروط القبول للخرسانـة :

أن لا يقل معدل قوة التحمل عن درجة الخرسانة المطلوبة.

ان لا تزيد نسبة التفاوت 20% عن المتوسط لقوة تحمل المكعبات.

ان لا يقل قوة تحمل أي مكعب عن 85% عن درجة الخرسانة المطلوبة.

في حالة عدم تحقيق شروط القبول للخرسانة على المقاول ان يقوم بأخذ عينات لبية ( كورات ) وحسب المواصفات العامة بند رقم 322/2/ج .

أعمال حديد التسليح الإنشائي:

يجب أن تشمل أسعار حديد التسليح الإنشائي ما يلي :-

ثني الحديد وأسلاك الربط .

كراسي المسافة والمباعدة البلاستيكية Plastic  Chairs  and Spacers

تأمين قضبان التسليح من جميع القياسات في جميع المواقع وعلى جميع الارتفاعات، ولا يسمح بأي زيادة عن الأطوال المبينة على المخططات .

القص والهدر .

المخططات التنفيذية لحديد التسليح : على المقاول تقديم الجداول الخاصة بتنفيذ مخططات حديد التسليح(Bar-Schedule Binding) مبينا فيها أطوال وأوزان حديد التسليح لممثل المهندس بغرض اعتمادها قبل التنفيذ

عمل الأساور الخشبية اللازمة لتثبيت حديد الأعمدة من الجهة العلوية بالإضافة إلى وضع البسكوت على جوانب الطوبار وعلى ارتفاع جوانب العمود.

توحيد درجة الحديد المستعملة لكافة العناصر الإنشائية لكل مجموعة إنشائية للأعمال الهيكلية.

تشمل أسعار شبك التسليح الجاهز الطيات المتراكبة LOPS.

يقوم المقاول بإجراء فحص لكل إرسالية حديد يتم توريدها للموقع و/أو حسب تعليمات المهندس ويشمل الفحص إجراء الفحوصات التالية:

تحديد إجهاد الخضوع ومقاومة الشد.

الاستطالة.

أقل قطر للثني.

وذلك وفقاً للمواصفة القياسية الأمريكية ( ASTM A615-80 ) أو المواصفة الأردنية ( م.ق.أ/2126/2016 ).

أعمال الطوب والحجر

أعمال الطوب الإسمنتي:

يجب أن تشمل أسعار أعمال بناء الطوب على ما يلي:

العمل في جميع الأصناف والأشكال في جميع المواقع وعلى أي ارتفاع.

مونة البناء والتكحيل.

قص الإغلاق.

عمل الفتحات والثقوب والفراغات اللازمة لمختلف التأسيسات الإكمالية للمشروع وعلى المتعهد إعادة إغلاق الأماكن الباقية.

تحضير الأوتاد والخوابير وخلافه من أعمال تأسيسية يلزم تحضيرها للأعمال الإكمالية للمشروع.

يرطب الطوب بالماء قبل استعماله ولا يجوز البناء بالطوب الجاف كما على المتعهد رش الجدران بالماء بعد بناءها لمدة ثلاثة أيام متوالية ولا يجوز استعمال الطوب المكسر أو المشقق والغير ناجح مخبرياً.

يجب تكوين الفراغ ( cavity  ) بين الجدران المزدوجة ويجب رفع جزئي الجدار سوياً ولا يجوز رفع أحد الجزئين عن  الآخر أكثر من 40سم.

تقديم جميع المرابط المعدنية.

المحافظة على خلو منطقة الفراغ ( cavity ) خالية من أي مواد قد تتساقط أثناء التنفيذ وذلك للمحافظة على منطقة العزل.

يجب أن تكون جميع الحلول الأفقية متوازية ومستوية والحلول الرأسية عمودية ومتخالفة ويجب تعبئة الحلول كلياً بمونة الإسمنت وبعد ذلك يتم تحرير الحلول بعمق ( 3 ) ملم أولاً بأول أثناء البناء لتماسك القصارة ويجب أن تكون الحلول متساوية في البناء الواحد ولا تقل عن ( 6 ) ملم ولا تزيد عن ( 15) ملم.

استعمال طوب مصمت لمناطق السلاحات والأبواب والشبابيك وبالقياسات التي تناسب سماكات الجدران وأسفل براطيش الشبابيك.

تكال أعمال البناء بالطوب بالمتر المربع ويكون الكيل هندسياً بعد حسم جميع الفراغات والفتحات والتي تزيد مساحتها عن ( 0.10 ) متر مربع.

القموط والجلسات الخرسانية وحديد تسليحها حول فتحات الشبابيك والأبواب والنهايات محملة على سعر المتر المربع من الطوب ولا تحسب كأعمال إضافية أو كعلاوات وتكون الخرسانة المستعملة درجة 20".

يتم بناء جدران الطوب حسب ما هو وارد في الفقرة 617 من المواصفات الفنية العامة.

أعمال القصارة

تشمل أسعار القصارة الأعمال والمتفرقات التالية :-

تقديم جميع المواد اللازمة مع المصانعة وتكاليف النقل إلى الموقع وضمن الموقع.

العمل في تحضير المساحات والمواقع التي سيتم عليها الأعمال .

تحرير حلول البناء وتخشين السطوح الملساء بالنقر قبل المباشرة بالقصارة لضمان تماسك المونة.

العمل بمختلف قياساته وعلى جميع المساحات وفي جميع المواقع وعلى جميع الارتفاعات.

إعطاء الوجه النهائي المعتمد والعمل أفقيا وعاموديا وعمل الميلان في جميع الاتجاهات المطلوبة وعمل التصليحات بعد جميع الأعمال.

العمـل فـي الاقنيـة وحـول الحلـوق والبراويز والبيش المعدنية وفوق الشبك المعدني وحول الفتحات والمصافي وما شابه ذلك.

إنهاء الحروف ذات الشكل المستدير أو المشطوف أو الفرزات وما شابهه.

عمل الوصلات بين السطوح الرأسية والافقية سواء كانت مستوية أم مائلة.

المخاليط المضافة سواء الملينة للمونة أو المانعة لنش الماء.

عمل الودعات اللازمة وبشكل يضمن عدم ظهور تشققات على جوانبها.

ضمان جودة مصنعية القصارة الخارجية من خلال عمل البقج للحصول على الاستقامات والاستواءات والشاقولية لجميع الواجهات والزوايا الخارجية.

يتم عمل اعتبار كميات الشبك المستعملة في حالة وجود سماكات للقصارة مشمولة ضمن سعر م2 للقصارة سواء داخلية أو خارجية.

يتم عمل ودعات عرضية لسلاحات الابواب والشبابيك لضمان الشاقولية والاستواء والتعامد العرضي مع الواجهات الداخلية والخارجية.

تحسب أعمال القصارة بالمتر المربع كيلاً هندسياً وفقا للمساحة التي هي على اتصال بالقاعدة بعد حسم جميع الفراغات التي تزيد عن ( 50,.) متر مربع، وتكال سلاحات الشبابيك والأبواب مع أعمال القصارة الداخلية.

المواصفات الخاصة بالزوايا والشرائح الشبكية المعدنية لأعمال القصارة:

ASTM 525/71 G60

ASTM C847/77

ASTM 366-68

ASTM A566-68

ASTM A 529 G90

OIN 17/62 Grade Stozz

يكون عرض الشرائح الشبكية الأدنى 150 مم ويزداد حسب وضعه الخاص بأنظمة الخدمات المخفية وبموافقة المهندس المشرف.

يكون عرض الزوايا الشبكية 75 مم.

يكون سماكة الصاج 0.5 مم على الأقل.

أعمال البلاط والرخام والأرضيات

تشمل أسعار أعمال التبليط والرخام والأرضيات الأعمال والمتفرقات التالية:

تقديم جميع المواد مع المصانعة وتكاليف النقل إلى الموقع وضمن الموقع والصب والتجهيز.

تقديم مونة التركيب المطلوبة وحسب اللون الذي يطلبه المهندس المشرف وتتكون من ( 300 )   كغم اسمنت لكل متر مكعب من الرمل ( ما لم يذكر خلاف ذلك ).

القطع والهدر.

الطمم بأي سماكة تحت البلاط الأرضي من الحصى والرمل بالحجم المناسب وطبقة خرسانة  درجة 10.

القطع الآلي للنهايات بالشكل المطلوب سواء نهايات مستقيمة أو مائلة أو دائرية

عمل أي طراز أو تشكيل مطلوب (pattern )

طبقات البطانة الخلفية من المونة الإسمنتية وبالسماكات اللازمة وباستواءات شاقولية وأفقية.

العمل في تحضير المساحات والمواقع التي سيتم عليها كافة الأعمال المختلفة.

العمـل بمختلف قياساتـه وعلـى جميع المسـاحـات وفـي جميـع الـمـواقـع وعلـى جميـع الارتفاعـات والأماكن المحصـورة ( إلا إذا ذكر خلاف ذلك ).

إعطاء الوجه النهائي المعتمد والعمـل أفقيا وعاموديا وعمل الميلان في جميع الاتجاهات المطلوبة وعمل التصليحات بعد جميع الأعمال.

العمـل فــي الاقنـيـة وحـول الفتـحـات والوصـلات والحـروف ذات الشكــل المستديـر والحروف المشطوفة والزوايا والمستديرة والاباريز وغيرها من أعمال مشابهه.

المخاليط المضافة.

المرابط المعدنية لربط كسوات الجدران بهيكل المبنى.

وضع الروبه والتكحيل باللون المناسب

القطع والعمـل حـول الفتحـات والمسـاحـات الغائرة والعمل حول المجاري والتمديدات والقطع الصحية والدرابزين ومصارف المياه وما شابه ذلك.

استعمال القطع الخاصة من البلاط الصيني والسيراميك عند التقاء الزوايا والتي أطرافها نصف دائرية.

تأمين الحماية المناسبة للبلاط الأرضي وبلاط الجدران والرخام بكافة مواقعها من الأوساخ وتساقط المواد والتجريح والخدش وضمان استمرارية نفس اللمعة كما تمت الموافقة عليها مسبقا.

تحسب أعمال التبليط ما عدا النعل بالمتر المربع وفقا للمساحة التي هي على اتصال بالقاعدة على أن لا تحسم الفراغات التي تقل عن (50, م2 ) والكيل هندسي.

أعمال المنجور

تشمل أسعار بنود أعمال المنجور والتركيبات الخشبية على:

تقديم مخططات الورشة التنفيذية المعتمدة   Shop Drawings

الخشب على اختلاف القياسات والاطوال.

الوصلات والتقطيع والهدر.

أعمال المنحنيات والانحدارات وأجور مصانعتها.

عمل الثقوب والزوايـا والحـروف الدائريـة والشطـفـات والفـرزات والوصلات والاخاديد وغيرها من أعمال مشابهه ومتممه.

ثقب الخرسانة أو الطوب أو الحجر وتركيب الخوابير وعمل التصليحات اللازمة بعدها.

طبقتين من الدهان الواقي على جميع أوجه الخشب الغير مكشوفة.

تحضير الأوجه لأعمال الإنهاء.

البراويز السفلية وخشب التثبيت والسندات.

الدهان لإعطاء طبقة النهو المطلوبة.

الخردوات المعدنيـة اللازمـة والمبينـة في المواصفات وشروط العقد شاملة، التقديم والتركيب والقطع والتثقيب لها في أعمال النجـارة، التثبيت المـؤقـت للخـردوات وإعادة التثبيت والتزييت وتكييـف أوضاع الأجزاء المتحركة والتزييت  والحماية.

تكييف جميع القياسات لأعمال النجارة لجعلها مناسبة مـع حالات الموقع بعد تنفيذ  هيكل المبنى وكذلك زيادة الأبعاد  للفتحات التي سيركب لها حلـق خلفـي لتكـون  الاقيسـة داخل الحلق الخلفي حسب أقيسة الفتحة المصممة والمثبتة على المخططات .

الزجاج المطلوب مع البيش المناسبة .

الصيانة  كامل المدة المطلوبـة واستبدال أي من القطع التي يظهر بها أي من عيوب أو فتلان خلال فترة الصيانة

تثقيب الجزء العلوي للمفصلات بثقوب صغيرة للتزييت وبموافقة المهندس المشرف.

يجب أن تكون فصالات الأبواب ستانلس ستيل.

الغالات ( الزرافيل) : تكون سلندر لكافة الأبواب صناعة أوروبية نوع فورمات أو دورما أو يونيون أو ما يعادلها مع زرافيل خاصة للحمامات من نوع المقبض الكروي KNOPSET ستانلس ستيل مزودة بإشارة.

الأيدي: تكون من صناعة أوروبية من نفس ماركة الزرافيل المعتمدة لكافة الأبواب ذات مقطع دائري قطر 19 ملم ستانلس ستيل.

المزاليج (اللقاطات): يركب لكل باب مكون من درفتين لقاطة علوية وسفلية مخفية ومن أشهر الماركات ومن الستانلس ستيل.

لا ينظر في اعتماد أي مادة معادلة إلا إذا ثبت صراحة عدم القدرة على توفير المادة المنصوص عليها صراحة من قبل الوكيل أو الموزع.

الأسعار لحلـوق الأبواب تشمـل بالإضافة لما ذكر سابقا، المرابـط المعـدنيـة المجلفنه لتثبيت الحلوق

الكيل للابواب بالمتر المربع من بداية الكشفة حتى نهاية الكشفة (ما لم يذكر خلاف ذلك).

الأعمال  المعدنية والالومنيوم  والـ P.V.C:

يجب أن تشمل أسعار الأعمال المعدنية المتفرقات التالية :

تقديم مخططات الورشة التنفيذية المعتمدة  ( Shop  Drawings   ) .

تقديم عينات لجميع المقاطع المعدنية ومقاطـع الـ P.V.C  المراد استعمالها والإكسسوارت اللازمة لكل عمل وكذلك تقديم نموذج بالحجم الكامل لقطعة أو قطع من أعمال الـ P.V.C  أو الحديد يحددها المهندس .

النقل والرفع والتثبيت باسافين وما شابه ذلك.

العمل في أي مكان في المشروع وعلى أي ارتفاع.

القيام بتنفيذ أي أعمال دائرية .

التجميع والتوصيل واللحام والصقـل والتثقيب لأحكام التركيب سواء بالجدران أو الأرضيات وتعبئة الثقوب وتركيب البراغي والتبشيم.

أدوات التثبيت والأسافين مع التثبيت والتركيب في المكان المحدد.

الهياكل الثانوية والتدعيمات الخلفية وعمل التصليحات اللازمة والحلوق الإضافية.

الخردوات المعدنيـة اللازمة والتثبيت المؤقت للخردوات واعادة التثبيت .

دهان ضـد الصدأ في المعمل أو طلاء طبقتين من الدهان المانع للصدأ قبل التركيب وإكمال الدهان بحسب المواصفات أو الشروط الخاصة.

الحقن بمواد خاتمة

مقابض اليد للدربزينات ( الكوبستات ) ما لم يذكر خلاف ذلك.

يتم تجميع النوافذ والابواب والبراويز الـ P.V.C والالمنيوم والمعدنية فـي المعمـل ومقوى حسب المخططات ومتطلبات ومستلزمات  العمل كاملــة مـع المفصـلات والزوايا وادوات التثبيـت ويجـب حمايـة جميـع وحـدات الـ P.V.C والالمنيـوم مــن الانشاءات الملاصقة وتسليمها بحالة ممتازة دون الظهور من أي مواد عالقة عليها.

تأمين صلابة كافية للنوافذ التي ليست لديها هيكل إنشائي تثبت عليه.

يجب أن تكون جميع النوافذ والأبواب صامدة لفعل العوامل الجوية.

جلخ وحف كافة النتوءات الناتجة عن اللحام وإزاحة قشرة اللحام والمحافظة على استواء ونعومة القطع .

عمل ثقوب صغيرة في جزء المفصلات العلوي لتزييت الأبواب.

تكون مادة الصنع لمادة الـ P.V.C من البولي فينيل كلورياد U.P.V.C MODIFIED والتي تتكون أساسا من مادة الرزن K 68 مضافا اليها العديد من المواد مثل TITANIUM U.VSATABLIZERS , I MPACT MODIFIERS .

جميع قياسات الأعمال المعدنية يجب أن يعاد كيلها لجعلها مناسبة مع حالات الموقع بعد تنفيذ الهيكل.

لا ينظر في اعتماد اى مادة معادلة الا اذا ثبت صراحة عدم القدرة على توفير المادة المنصوص عليها صراحة من قبل الوكيل أو الموزع.

يشمل السعر جميع الإكسسوارات اللازمة لشبابيك الألمنيوم من أشرطة وجلد وفراشي لصد الماء والهواء.

أعمال  الطراشة والدهان:

تشمل أسعار الدهان على الأعمال والمتفرقات التالية :

تحضير وتنظيف جميع السطوح المراد دهنها .

العمل على جميع الاشكال والمساحات بما فيه المساحات الضيقة .

العمل بعدة الوان.

القطع عند الحروف أو الاطراف والحف والتنعيم بين الطبقات اوالاوجه .

أعمال الحماية وتنظيف الزجاج أو البلاط أو المنجور الخشبي الملطخ واعادة دهن كل الأعمال المتضررة

معالجة جميع التشققات بعد حفرها وأخذ موافقة المهندس المشرف على طريقة الحفر وشكله وأسلوب المعالجة بالمواد المعتمدة سابقا من قبل المهندس.

يمنع منعا باتا خلط الدهان بأي مواد في الموقع مثل التنر أو النفط ويتم استعمال الدهانات حسب تعليمات الشركة الصانعة.

تكال أعمال الدهان للسطوح كيلاً هندسياً بالمتر المربع لواقع السطوح التي جرى دهانها بالموقع بعد حسم جميع الفراغات والفتحات والشفرات التي تزيد مساحتها عن ( 0.50 )	متر مربع .

لا ينظر في اعتماد اى مادة معادلة إلا إذا ثبت صراحة عدم القدرة على توفير المادة المنصوص عليها صراحة من قبل الوكيل أو الموزع .

أعمال العزل على السطوح:

تشمل أسعار السطح ومنع الدلف ما يلي:

تنظيف وتحضير المساحات.

العمل في جميع المساحات وعلى أي مستوى.

الأطراف الانسيابية والدائرية والأفاريز والحروف الحادة.

القطع والطيات المتراكبة والطبقات اللاصقة بين الاطراف المتراكبة.

الإعداد للميول والانحدارات المتقاطعة على اختلاف انواعها .

العمل حول الفتحات والاقنية ومصارف المياه وما شابه ذلك .

القيام بعمل الفتحات والعمل حول الزوايا والصفائح المعدنية والمواسير والفتحات ووضع الحلقات حولها .

تحسب كل الأعمال المانعة لتسرب المياه والسطح بالمتر المربع ولا تحسب الطيـات المتراكبـة ولا تحسم الفراغات التي تقل مساحتها عن ( 25,.م2 ) .

الأعمال الخارجية:

- تكون مواصفات وشمولية أسعار كافة الأعمال المدرجة ضمن هذا الباب كما نصت عليه ضمن أبواب الأعمال الداخلية وللبنود المشابهة لها ما لم يذكر خلاف ذلك لاحقاً في هذه المواصفات أو في نص البند في جداول كميات الأعمال الخارجية.

أعمال الحفريات:

أعمال حفريات التسوية والأساسات:	تكون بنفس مواصفات وشمولية أسعار بنود الحفريات الداخلية.

أعمال الخرسانة:

تكون بنفس مواصفات أعمال الخرسانة الداخلية الواردة في هذه المواصفات وحسب تحديد المخططات وجداول الكميات مع الأخذ بعين الاعتبار ما يلي للبند التالي:

أعمال الخرسانة العادية والمسلحة للأرضيات : تكون حسب شمولية أسعار ومواصفات الخرسانة في الأعمال الداخلية مع مراعاة أن يكون الصب على مراحل لتأمين فواصل الصب والإنكماش وحسب تحديد المهندس المشرف والمواصفات العامة والكود العربي.

أعمال البلاط والأرضيات

أعمال الكندرين تكون من الخرسانة صنف أ بقوة كسر 25ن/ملم2 وحمل الكسر المستعرض الأدنى 35 كيلو نيوتن حسب ما هو وارد في الجدول 3/24 صفحة ( 3-119 ) من المواصفات الفنية العامة ويجب أن يكون الكندرين ذو وجه ناعم فيرفيس ويجتاز بنجاح الفحوصات المذكورة أعلاه ويشمل السعر خرسانة التصفيح وخرسانة النظافة أسفل الكندرين درجة 15 مع المونة والكحلة والإيناع والتنظيف بعد التركيب وتشمل الحفريات والطمم الخاصة به وكافة ما يلزم حسب المخططات.

أعمال الزفتة

توريد والقيام بطمم مواد ( Base Course ) المفحوص والمعتمد مخبرياً حسب السماكة المحددة بجدول الكميات بعد الدحل الجيد من الصنف ( أ ) ومطابق للمواصفات الأردنية للطرق والجسور لعام 1991بند ( 200 ).

رش الإسفلت ( MC -70  ) .

يكون الإسفلت المستعمل للخلطات نوع 80/100 .

فرش طبقة من خلطة إسفلتية بسماكة صافية 7سم بعد الدحل الجيد على أن تكون الخلطة بزرة ناعمة.

يجب تنفيذ جميع البنود أعلاه حسب مواصفات وزارة الأشغال العامة وتعليمات المهندس بالميل المبين على المخططات من أجل تصريف مياه الأمطار.

تكون طبقة الـ MC حسب البند رقم ( 310 ) وطبقة الخلطة الإسفلتية الساخنة حسب البند (317) من المواصفات القياسية الأردنية للطرق والجسور لعام 1991.

قبل المباشرة بوضع الخلطة الإسفلتية يجب أن يتم وضع جهاز دك قوالب مارشال في موقع العمل لأخذ العينات مع تحديد منطقة العمل المنجزة.

المواصفات الفنية لأعمال تعبيد وتزفيت الطرق والساحات:

تعتبر المواصفات الفنية لأعمال الطرق الصادرة عن مديرية الطرق بوزارة الأشغال العامة عام 1991 مرجعا لأعمال تعبيد وتزفيت الطرق والساحات واحد وثائق العقد مع مراعاة ما يلي على سبيل المثال لا الحصر:

أعمال التسوية والدحل القسم ( 106 ) ( Section 106 Embanckment.

أعمال رش الماء القسم ( 108 ) ( Section 108 Wattering  .

فرشيات النحاته تحت الأسفلت القسم ( 200 ) Section 200 Aggregate Base

الوجه الأساسي للاسفلت ( القسم 310 ) Section 310 Bitiminous Prime  Coat .

الاسفلت الخلط القسم (317 صفحة 108) Section 317 Bituminous Plant Mix Surfacing

الاسفلت :

يكون الاسفلت المستعمل للخلطات نوع 80/100

يكون الاسفلت المستعمل للوجه الأساسي تحت الاسفلت الخلطي من M.C.1   .

الخلطة الاسفلتيه

تكون سماكة الخلطة الاسفلتيه حسب السماكة المبينة في جداول الكميات وتعتبر هذه السماكة هي السماكة الصافية بعد الدحل .

وفي حالة زيادة السماكة عن 7سم تعمل الخلطة على طبقتين مع وجه لاصق من الاسفلت بين الطبقتين وتزاد السماكة في الأماكن اللازمة وتشطف الجوانب الخارجيه للخلطة المفروشة بميل 2/1 ويجب عملها بنفس الوقت مع أعمال الخلط .

تكون نسبة الاسفلت المستعملة بموجب البند ( 317 )، 2، 1 هي 5.5% بالوزن قابلة للزيادة أو النقص بنسبة 1% ويتم تحديد نسبة الاسفلت المطلوبة من قبل المهندس بعد اجراء الفحوص الاختبارية اللازمة .

قبل المباشرة بوضع الخلطة الإسفلتية يجب أن يتم وضع جهاز دك قوالب مارشال في موقع العمل لأخذ العينات مع تحديد منطقة العمل المنجز.

المواصفات و الشروط الخاصة بالاعمال الكهربائية:

عام:

جميع الأعمال الكهربائية للمشروع مبينة على المخططات المعدة لذلك وحسب تعليمات المهندس المشرف.

تقديم المواصفات والكتالوجات والعينات المنوي استعمالها لأخذ الموافقة الخطية عليها قبل  بدء التركيب بما لا يقل عن اسبوعين وإذا رفضت العينات لا يعد مبرراً للتأخير. وتعتبر العينات تالفة إذا استخدمت للفحص ، أما إذا لم تستخدم فيتم إعادتها عند نهاية التنفيذ ويتحمل المقاول تكاليف الفحص إذا تطلب الأمر ذلك ، كما يتم الفحص لدى الجمعية العلمية الملكية وعلى المقاول تأمين العينات التي يتطلبها الفحص .

تكون جميع المواد الكهربائية المستعملة مطابقة للمواصفات المحلية أو البريطانية (BS) عند عدم وجودها ، أو الألمانية (DIN) إن كانت بلد المنشأ .

تتم جميع الأعمال الكهربائية حسب ( دستور البناء الوطني الأردني ) الصادرة عن وزارة الأشغال العامة والإسكان  المجلد الثالث والعشرون (خمسة أجزاء ) والمواصفات الفنية للمباني / الأعمال الكهربائية.

يكون السعر شاملاً جميع الأعمال والمواد اللازمة للبند الوارد في جدول الكميات حتى انتهاء الفحص والتشغيل في الموقع وبشكل كامل.

يكون المقاول مسؤولاً عن تطبيق شروط ومواصفات وتعليمات شركة الكهرباء الأردنية وكذلك شركة الاتصالات الأردنية والدفاع المدني وان اختلفت عن شروط العطاء .

تعتبر المواصفات والمخططات وجدول الكميات ومواصفات وزارة الأشغال العامة  الواردة سابقا جزء من العطاء ومكملة لبعضها البعض.

على المتعهد قبل البدء بتنفيذ الأعمال الكهربائية بأسبوعين على الأقل تقديم مخططات تنفيذية (WORKSHOP DRAWINGS) لدراستها وإقرارها من المهندس المشرف ولا يتم التنفيذ إلا بعد أخذ الموافقة عليها، وبعد انتهاء الأعمال تقديم مخططات التنفيذ حسب الواقع (AS BUILT DRAWINGS) (الأصل مع نسختين ) ، وتكون الكتابة عليها بخط طباعة أو خطاط .

على المقاول إجراء كافة الفحوصات والتجارب التي تطلب منه أثناء سير العمل أو بعد الانتهاء منها وعلى المقاول إزالة الأعمال التي لم تنجح وإعادة عملها والأضرار الناتجة عنها .

على المقاول ارفاق كافه الفحوصات ل (IP )  من الجمعيه العلميه  الملكيه  او من جهه مختصه لفحص (IP )  لجميع المواد التي يطلب لها  IP

نظام توكيد جودة للمواد والأنظمه الكهربائيه يتضمن ما يلي :

- فحص طرف ثالث لأية مواد أو أنظمه كهربائية للتأكد من مطابقتها لمواصفات العطاء وعلى نفقة المقاول ويجوز أن يكون المصنع الذي يصنع الأنظمه والمواد خاضعآ لفحوصات الطرف الثالث شريطة قناعة المهندس  ( مهندس العقد ) أو المهندس  المشرف ويشمل ذلك نظام الصوتيات وكل الأنظمه الكهربائية .

- فحص طرف ثالث لكل من العازلين وال Durability  لمفاتيح الإناره والأباريز والقواطع وعلى نفقة المقاول ويقبل فحوصات الجمعيه العلميه الملكيه .

المواصفات الفنية

تستعمل الأسلاك والكوابل النحاسية المعزولة بمادة (PVC) ويكون تحمل الأسلاك (450) فولت، والكوابل (750) فولت على الأقل ،أما أسلاك الفولتية المنخفضة (الهاتف والأجراس ) فيجب أن تتحمل مالا يقل عن (60) فولت .

تستعمل المواسير المصنوعة من مادة (PVC) المقوى بالأقطار المناسبة بحيث لا تزيد عامل الامتلاء عن 40%  وتكون القطع اللازمة من نفس النوع المفف (Coupler) والأكمام (Slaves) والملبوشة (Male push) والأساور (Adapters) والعلب (Boxes) ويستعمل صمغ اللحام المناسب لوصلها .

في حالة استعمال المواسير المعدنية (بنسر) تنظف نهايات المواسير وتسنن بالة خاصة وتوضع أكمام نحاسية في نهاية كل ماسورة .

ولا يجوز تثبيت المواسير على الجدران أو الأرض بالطين إذ تثبت بمرابط خاصة ولا يجوز استعمال المواسير كأداة حمل أو ارتكاز.

ويتم ثني المواسير بواسطة أداة خاصة لا يتغير قطرها عند نقاط الثني كما لا يجوز ثني الماسورة بين نقطتين أكثر من مرتين دون استعمال علب السحب .

عند مرور المواسير بفواصل التمدد تستخدم وصلة خاصة مرنة (Flexible) .

إذا تقاطعت الأعمال الكهربائية مع الأعمال الأخرى تكون التمديدات الكهربائية فوق  التمديدات الأخرى.

يتم تركيب المواسير والعلب والمفف والملبوشات ولحامها على طوبارالسقف قبل صب  الخرسانة حسب المخططات الكهربائية المعدة للمشروع قبل وقت كاف لعرضها على المهندس المشرف في الموقع وأخذ موافقته الخطية على الصب.

يجب تأمين الفتحات اللازمة في الخرسانة المسلحة والحاملة قبل صب الخرسانة ويكون الحفر عمودياً ولا يجوز الحفر أفقياً أو مائلاً أكثر من متر واحد ، ولإعادة الوضع يجب استخدام شبك معدني على طول الحفر بحيث لا يقل عن 5سم على كل جانب من جوانب الحفر .

يستخدم في التمديدات النظام الحلقي (Loop – in) ولا يجوز قطع الحيادي إلا عند نقطة الإنارة أو الإبريز أو الجهاز ، كما لا يجوز قطع الفاز إلا في المفتاح أو الإبريز .

تكون علب المفاتيح والأباريز ولوحات التوزيع على مستوى القصارة تماماً كما تكون مثبتة بشكل أنيق ولا يشوه منظر الجدران كالإعوجاج أو ظهور قسم منها خارج القصارة.

تكون علب الإنارة دائرية بها ثقوب قابلة للفتح من الأرضية إن كانت مثبتة في الربس أو ذات امتدادات جانبية بالعدد المطلوب إن كانت ستثبت في البلاطة أو الجدران كما تكون علب السحب والمفاتيح والأباريز مربعه أو مستطيله حسب الغاية من استعمالها وتكون جميع العلب ذات وصلات نحاسيه في نقاط ربط البراغي .

يجب التقيد التام  باستعمال ألوان الأسلاك وربطها بالفازات ولوحات التوزيع الرئيسية والفرعية والمفاتيح والأباريز ووحدات الإنارة . وتسحب الأسلاك داخل المواسير بعد القصارة بطريقة فنية صحيحة ( باستقامة الماسورة ) بحيث لا يؤدي هذا العمل إلى إجراء أي جرح أو تلف لعازل الأسلاك أو المواسير وقطعها الأخرى  .

ويمنع منعاً باتاً وصل الأسلاك داخل المواسير مهما كانت طريقة الربط ، ولا يقبل ثني الأسلاك على بعضها وربطها بواسطة شريط لاصق ( TIP)  .

تكون خزانة العدادات ولوحة التوزيع من حديد الصاج بالسماكة المنصوص عليها وإلا تكون السماكة ( 1.2) مم مدهونة بطبقة أساس مانعة للصدأ وطبقتي دهان حراري أو الكتروستاتيك لا تقل سماكته عن 90 ميكرون ولا يسمح أي جزء من المعدن بدون دهان بما فيها الحواف .

تكون جميع التمديدات مخفية إلا إذا ذكر غير ذلك صراحةً في العطاء .

تكون جميع المواد من أجود الأصناف قادرة على تحمل الظروف المحيطة بها وتأدية الغرض المطلوب منها وليس لبلد المنشأ أي امتياز .

لا  يجوز تركيب هياكل لوحات التوزيع قرب المياه أو الأماكن الرطبة أو النار أو المواد  القابلة للإشتعال .

التأريض :

يتم اختيار موقع ذو تربة مناسبة الرطوبة، سهل الوصول إليها يبعد عن طرف جدار المبنى بما لا يقل عن طول القضبان التي تدق في التربة بدقات خفيفة متتالية.

يوضع فوقه مانهول قياس (40×40×25) سم (من الداخل ) من الخرسانة أو البلاستيك  وله غطاء معدني أو إسمنتي مسلح يمكن فتحه وإغلاقه  ، وبمستوى الأرض المحيطة به ويكون قضيب التأريض أو شبكة التأريض من الحديد المغطى بالنحاس الأحمر المخمر وتربط نهايته العليا مع الموصل بواسطة مربط خاص ولا يجوز أن يربط مباشرة حسب المخطط المرفق .

تكون التمديدات والمفاتيح والأباريز والوحدات المركبة خارج المبنى مقاومة لتسرب الماء ومناسبة للظروف المناخية وإن لم ينص جدول الكميات على ذلك .

المواد وقياساتها  :

تكون المواسير بقطر 20مم.

تكون أسلاك الإنارة (2.5) مم2 والأباريز وسخان الماء (4) مم2 ما لم يرد خلاف ذلك.

القياسات :

- ارتفاع نقطة الإنارة فوق المغسلة 1.85 م وفوق منتصفها .

- ارتفاع نقطة الإنارة فوق الباب 2.20 م .

- ارتفاع المفاتيح عن سطح البلاط 1.35 م .

- ارتفاع  الأباريز 0.45 م فوق سطح البلاط ماعدا المطابخ فيكون 1.35 م ما لم يرد خلاف ذلك .

- ارتفاع قاعدة لوحة التوزيع 1.8 م .

- بعد المفتاح عن كشفة الباب 0.20 م وإذا كان تحته إبريز يكون بنفس البعد أي تقع على خط شاقولي واحد ويبعد الإبريز عن الزوايا 0.45 م .

- يكون المفتاح عكس اتجاه فتح الباب أما في الأبواب ذات الظرفتين المتساويتين فيكون على اليسار ، أما إذا كانت الظرفتين مختلفتي العرض فيكون بجانب الظرفة الصغيرة ، وعلى يمين أبواب الجرار .

- تركب أغطية المفاتيح والأباريز ولوحات التوزيع ووحدات الإنارة بعد الانتهاء من أعمال الدهان والطراشة بحيث تكون نظيفة .

المفاتيح والأباريز :

المفاتيح :

جهد التشغيل 240 فولت

معدل الجهد 250 فولت

التردد 50 هيرتز

التيار (10) أمبير

الأباريز :

جهد التشغيل 240 فولت .

معدل الجهد  250 فولت .

التردد 50 هيرتز .

التيار (13) أمبير ما لم يرد غير ذلك

ثلاثي التوصيل ( فاز – حيادي – أرضي )

شمولية الأسعار

البند يعني البند في المواصفات المرفقة .

نقطة الإنارة :

تشمل نقطة الإنارة المواد والأعمال اللازمة من مواسير (PVC) أو معدنية حسب البند رقم 2 والأسلاك حسب البندين (16،1-ج) ، والعلب حسب البند 7 و 8 والمفاتيح على اختلاف أنواعها (طريق واحد أو طريقين أو مصلب أو كبسة ذاتية الرجوع ) ، والتي تبينها المخططات وليس لعددها أي علاقة بعدد النقاط ، أما إذا لم تبين المخططات هذه المفاتيح فللمهندس الحق في طلب مفتاح لكل نقطة إنارة ولا يجوز الجمع بين فازين في علبة واحدة أو مفتاح ويكون لكل فاز علبة ومفتاح ، أما الفاز الواحد فيمكن جمع أكثر من نقطة إنارة في نفس العلبة وعندها يكون المفتاح مفرد أو مزدوج أو ثلاثي وتضاف علبة أخرى إذا زاد عدد الدارات عن ذلك .

أما الأعمال فتشمل تجهيز المواسير قبل الصب عليها أو الحفر لها حسب البنود 4 و 5 ويجب تلافي مرور المواسير في الأعصاب ، كما يتم تمديد المواسير فوق الربس وتوصيل الأسلاك حسب البند 6 و 9 حتى لوحة التوزيع وتجريبها لتعمل النقطة بشكل فني امن .

الأباريز :

يعني الإبريز المأخذ الكهربائي أو مأخذ الهاتف أو مأخذ التلفاز أو مأخذ الكمبيوتر أو أي مأخذ منصوص عليه في جدول الكميات ولا يجوز الجمع بين أي نوعين من الأباريز السابقة في ماسورة واحدة ويجب التمييز بينهما بشكل واضح ولا يقبل الاستعمال بطريق الخطأ .

يشمل الإبريز المواسير وتمديدها حسب البنود 2،3،5 والعلب حسب البند 7 و 8 والأسلاك أو الكوابل وتمديدها حسب البندين 1 ، 9 ، ويكون مقطعها حسب ما ورد في المخططات، وإذا لم يكن واضحاً يكون حسب البند 16 .

ويشمل السعر الإبريز نفسه بحيث يكون من نوع ذو القطعة الواحدة مصنوع من مادة البكليت يثبت بواسطة برغيين أفقيا .

يكون إبريز الكهرباء ذو توصيل ثلاثي (فاز ، حيادي ، أرضي) وتثبيتها بالعلبة حسب البند 7 ويكون الفاز الأيمن والحيادي الأيسر ، وإذا كان الإبريز يعمل بواسطة مفتاح فيوصل به الفاز فقط .

ويكون إبريز الهاتف من نوع (RJ-11) ، وتكون الكوابل حسب البند 1 .

أما إبريز التلفاز فيكون ذو وصلة خاصة تداخليه بشكل محوري وتكون الفتحة في الوسط يوصل بها كيبل محوري لا يتغير مقطعه بالضغط عليه.

لوحة التوزيع :

وتعني اللوحة التي تحتوي القواطع الفرعية التي تغذي الدارات المختلفة مباشرة ، تكون لوحة التوزيع معدنية غاطسه ما لم يرد نصاً صريحاً بخلاف ذلك وتكون من الصاج سماكته (1.2)  مم مدهونة بطبقة أساس مانع للصدأ وطبقة دهان حراري أو دهان الكتروستاتيك .

تتكون اللوحة من الأجزاء التالية :

العلبة

الغطاء

الباب

القاطع الرئيسي والقواطع الفرعية.

العلبة :

تجهز العلبة بحامل عازل لمجمع الفاز (  Phase Buss Bar ) والباسبار نفسه ، ويكون مصنوعاً من النحاس المخمر بحيث لا تزيد كثافة التيار على المقطع عن  (2) أمبير/ مم2 ،  تركب علبة القواطع الفرعية دون الحاجة لأي قطع تثبيت بحيث يمكن فك أي قاطع دون الحاجة لفصل التيار عن اللوحة أو فصل التيار عن أي قاطع فرعي آخر ، كما تحتوي على قاعدة خاصة ومميزة للقاطع الرئيسي الذي يتم توصيله بخط التغذية والمجمعات .

مجمع الحيادي ( Neutral Buss Bar ) يكون مقطعه كالسابق إضافة إلى وجود فتحات لا يقل عددها عن عدد الدارات إضافة إلى فتحة خاصة لخط التغذية ، مجهز ببراغي لربط الأسلاك أو الكوابل بإحكام ، ويكون معزولاً عن جسم العلبة .

مجمع الأرضي ( Earth Buss Bar ) وينطبق عليه ما ورد في مجمع الحيادي إلا أنه غير معزول عن العلبة ، للعلبة ثقوب مختلفة الأقطار غير نافذة يمكن فتحها بسهولة حسب مقطع المواسير المستخدمة .

الغطاء :

يثبت على العلبة بواسطة البراغي أو مرابط نابضة ويمثل وجه اللوحة الأمامي ، يحتوي على ثقوب تبرز منها مقابض القواطع الفرعية والرئيسية وتعزل التوصيلات عن مستعملها كما يوضع عليها أرقام القواطع والدارات التي يتم التحكم بها .

الباب :

يركب على الغطاء وله فصالتان ويمكن إغلاقه على الغطاء بواسطة مربط نابض أو بالبراغي  ، يوضع عليه في الداخل مخطط الدارات التي يتم التحكم بها ، ويمكن أن يكون معدنياً أو شفافاً .

إضافة لجسم اللوحة الوارد سابقا يشمل السعر القاطع الرئيسي المنصوص عليه في المخططات والقواطع الفرعية من نوع ( MCB ) وتوصيلاتها، كم و يشمل السعر تسمية القواطع والمخططات اللازمة والتي تبين جميع التوصيلات.

إذا زادت سعة اللوحة عن عدد القواطع المطلوبة تغلق فتحات القواطع بقطع ( pvc) خاصة بدون براغي .

لوحة القواطع (MDB) :

وتعني اللوحة الكهربائية التي تحتوي القواطع الرئيسية وتغذي لوحات توزيع أو لوحات تحكم كهربائية.

تكون لوحة القواطع من حديد الصاج سماكته لا تقل عن (2) مم ، تدهن بطبقة أساس مانعة للصدأ وطبقة دهان حراري أو الكتروستاتيك بحيث لا تقل سماكة الدهان عن (120) ميكرون ، أما إذا كانت خارجية فبالإضافة لما سبق يمكن أن يكون الدهان   (Epoxy ) ، تدعم اللوحة بزوايا حديد طولية وعرضية .

تثبت اللوحة على قاعدة خرسانية لا تقل سماكتها عن (15) سم ، وترتفع عن أرضية الغرفة (15) سم أيضاً إن كانت داخلية ، وإن كانت خارجية فترتفع (40) سم عن الأرض الطبيعية ، وإذا كان خلف اللوحة جدار فتكون القاعدة الخرسانية من ثلاثة جوانب ، كما تتم قصارتها بشكل جيد أو تلبيسها ببلاط مشابه لبلاط أرضية الغرفة .

يتم عمل الفتحات اللازمة لدخول وخروج الكوابل في أرضية أو سقف اللوحة ، حسب طبيعة التمديدات المطلوبة ، ولا تقبل التمديدات من جوانب اللوحة .

تتكون اللوحة من الأجزاء التالية :

الخانة الأولى : وتكون على يمين اللوحة أو يسارها حسب ورود خط التغذية الرئيسي ويركب فيها عداد شركة الكهرباء أو سلطة الكهرباء والقاطع الرئيسي وبالسعة التي تتطلبها الشركة ، وتتصل بفتحة إلى الخانة الثانية لا يقل قطرها عن قطر كيبل التغذية ، يركب على حواف هذه الفتحة بعد تنظيفها كسكيت لمنع جرح الكيبل ، وتكون الخانة جاهزة لإغلاقها بالرصاص من الشركة أو السلطة .

الخانة الثانية : وتكون في أعلى اللوحة إن كان التوزيع من الأسفل وعلى جانب الخانة السابقة إن كان التوزيع من الأعلى ، تحتوي على جسور معدنية تركب عليها عوازل لتحمل المجمعات ( Buss-Bars ) وهي ثلاثة فازات متتالية يليها الحيادي ، بحيث لا تزيد كثافة التيار عن ( 1.5 ) أمبير/ملم2 وأن لا تقل سعة المجمع عن (1.5) مرة سعة القاطع الرئيسي .

تغطى هذه المجمعات بلوح من الفيبر سماكته (4) ملم مثبت بالبراغي ، ولا تظهر المجمعات عند استعمال القواطع الأخرى ويكتب عليها تحذير بعدم رفعه إلا بعد فصل التيار عن القاطع الرئيسي .

الخانة الثالثة : تركب بها جسور معدنية تثبت عليها قواطع بالاستطاعة والعدد المطلوب ، من نوع (MCCB) ، تثبت القواطع إما بواسطة مجرى أو مباشرة على الجسر بواسطة برغيين دون الحاجة إلى أي قطع معدنية إضافية ، كما تحتوي الخانة على مجرى جانبي لمرور الأسلاك والكوابل المغذية والخارجه بحيث يمكن تتبعها بكل بساطة ووضوح ، ولا تكون عرضة للعبث أو تعيق أعمال الصيانة .

تغطى هذه الخانة بلوح من الصاج يظهر منه مقابض القواطع فقط ، يكتب عليها الجهة المغذاة من كل قاطع .

تغلق بواسطة ظرفتان لكل ظرفه فصالتان بحيث لا تزيد المسافة بين كل فصالتين عن 65 سم .

تثبت على هذه الظرف أجهزة قياس التيار والفولتية مع مفتاح اختيار ولمبات إشارة للفازات .

الخانة الرابعة : وتكون أسفل اللوحة والغاية منها عمل التوصيلات اللازمة ورفع التوصيلات عند الرطوبة والاحتفاظ بطول أسلاك أو كوابل احتياطية تغطى بلوح من الصاج محمي ضد الصدأ .

لوحة القواطع (SMDB):

- مماثلة للوحة القواطع MDB  باستثناء خانة عداد شركة الكهرباء.

شروط عامة :

تعتمد مواصفات وزارة الأشغال العامة – أخر طبعة للمجلد الثالث وما لحق بها من تعديلات وكذلك مواصفات شركة الكهرباء الوطنية الأردنية بالإضافة إلى أية مواصفات وتعليمات مذكورة في أي من وثائق العطاء كمرجع لغايات تنفيذ الأعمال الكهربائية ، وفي حال وجود تعارض بينها يحسم الخلاف برأي المهندس المشرف .

تخضع كافة الأعمال والمواد والتمديدات لموافقة المهندس المشرف قبل الشراء والتنفيذ وعلى المقاول تقديم كتالوجات ورسوم توضيحية وعينات للمواد المراد تركيبها في الموقع لأخذ الموافقة المسبقة عليها .

على المقاول قبل المباشرة بأعمال الموقع بثلاث أسابيع على الأقل تقديـم مخططات تنفيذيـة Work shop  محتوية على معلومات توزيع الأجهزة الكهربائية ومواقعها وطريقة التمديد وأقيسه المواسير والكوابل والأسلاك ومسارها ومستويات تمديدها وكل ما يلزم من معلومات تنفيذية وذلك لدراستها والموافقة عليها من قبل المهندس .

على المقاول تسمية مهندس الكهرباء المنفذ الذي سيتولى متابعة الأعمال الكهربائية بحيث يكون متفرغاً لهذا العطاء وموافق علية من قبل المهندس.

على المقاول وبناءً على تعليمات المهندس المشرف واعتمادا على المواصفات المعتمدة في العطاء إجراء كافة الاختبارات والفحوصات اللازمة خلال العمل وبعد الانتهاء منه للتأكد من سلامة التمديدات والأجهزة الكهربائية المختلفة ومطابقة ذلك للمواصفات . وعلى المقاول توفير أجهزة الفحص اللازمة بطريقته الخاصة وتقديم اعتمادها للمهندس المشرف للموافقة عليها قبل استعمالها .

على المقاول الالتزام بنوعية المواد المطلوبة والمنصوص عليها في وثائق العطاء ، ولا يتم النظر في اعتماد أي مواد أخرى معادلة إلا في حالة عدم توفر المواد المنصوص عليها في العطاء ، وذلك عن طريق تقديم إثباتات خطية بذلك من الوكلاء والموزعين ولهذه المواد في المملكة .

يجب على المقاول عنـد الانتهـاء من العمل تقديم مخططات حسب التنفيذ Built- As مدعمة بكافة ما يلزم من معلومات فنية ولن يتم تشكيل لجنة استلام أولية قبل تجهيز هذه المخططات .

يجب على المقاول عند الانتهاء من العمل تقديم كشف يبين كافة أنواع المواد التي استعملها في المشروع محتوياً على عناوين الوكلاء والشركات الصانعة والرقم ألمصنعي لهذه المواد وذلك لتقديمه إلى صاحب العمل للاستعانة به مستقبلاً عند الحاجة إلى إجراء الصيانة أو استبدال أي من هذه المواد .

كافة التمديدات التي تكون مخفية في الأسقف والجدران والأرضيات تتم باستعمال مواسير من بالأقطار المناسبة  البلاستك المقوى فئة (ب)  PVC Conduits, heavy gauge-class B  وكذلك العلب والحلقات والأكمام والمرابط المناسبة وحسب المواصفة البريطانية BS4607, Part1  لهذه المواسير تكون من نفس المادة .

كافة التمديدات الظاهرة والخارجية تكون عبر مواسير فولاذية مجلفنة حسب المواصفات  البريطانية  BS31,Class B وبالأقطار المناسبة

في حال تقاطع التمديدات الكهربائية مع أية تمديدات أخرى فان مستوى التمديدات الكهربائية يجب أن يكون دائما هو الأعلى مع الحفاظ على الحد الأدنى للمسافات لمطلوبة بينها حسب المواصفات المعتمدة للعطاء .

يجب الالتزام ننظام الألوان في كافة التمديدات (أحمر ، أصفر ، أزرق للفازات ، أسود للحيادي ، أخضر للأرضي ) مع مراعاة أن تكون كافة التمديدات الخاصة باللوحة الفرعية الواحدة وتوابعها ذات لون واحد فقط لخط الغاز.

يجب أن تكون دوائر الإنارة ، الأباريز ، الهاتف ، التلفزيون ونظام إنذار الحريق منفصلة عن بعضها في كافة مساراتها .

في كافة التمديدات الكهربائية . -يستعمل النظام الدائري LOOP SYSTEM

يمنع استعمال الشريط اللاصق نهائياً في أي من التوصيلات .

يمنع قطع خط الفاز في أي من التمديدات إلا في مفتاح الإنارة أو الإبريز.

يتم تجميع وترتيب الأسلاك والكوابل في اللوحات الكهربائية بواسطة مرابط بلاستيكية .

على المقاول ترقيم كافة التمديدات بتسلسل واضح وموحد لكافة اللوحات والدوائر وتثبيت هذا الترقيم على المفاتيح والاباريز واللوحات الفرعية والشبة الرئيسية والرئيسية وعلى العدادات الكهربائية باستعمال مواد خاصة للترقيم لا تمحى ، إضافة إلى تثبيت هذا الترقيم في مخططات AS BUILT

يمنع منعاً باتاً وجود أكثر من كوعين 900  متتالين على نفس مسار التمديدات الكهربائية وعند الاضطرار لذلك يجب تركيب علبة وصل بقياس مناسب بعد الكوع الثاني.

يشمل سعر النقطة ، إنارة اباريز ، تلفزيون ، هاتف كافة المواسير والأسلاك والمفاتيح والاباريز والعلب واليد العاملة والفحص ...الخ وكل ما يلزم لإنهاء العمل من اللوحة المغذية للنقطة ذاتها فيما عدا وحدة الإنارة فقط .

الكوابل التي تمدد في الأرض الطبيعية تكون مسلحة ، وتدفن على عمق لا يقل عن 70سم عن وجه السطح النهائي ، بحيث يراعي تمديد الكوابل على أرضية من الرمل الناعم لا تقل سماكتها عن 10 سم ومن ثم إعادة الطمم فوق الكوابل من الرمل الناعم بسماكة لا تقل عن 25سم مع وضع بلاطات خراسانية وشريطة تحذيري على طول مسار الكوابل ، ومن ثم إجراء الطمم بالمواد الطبيعية .

توضع علامات خراسانية بارزة لتوضيح أماكن الكوابل في الأرض كل 50 متر ، وعند تغيير اتجاه الكيبل .

عند مرور الكوابل المدفونة في الأرض من خلال شوارع وأرصفة يجب تمريرها من خلال UPVCمواسير بلاستيكية  ذات قطر مناسب مدفونة في هذه التقاطعات وعلى عمق لا يقل عن 70 سم من وجه السطح النهائي

المواد : يجب أن تكون المواد المراد استعمالها في أعمال العطاء مطابقة للمواصفات المبينة أدناه :

لوحات التوزيع : الرئيسية وشبه الرئيسية :

تكون هذه اللوحات مـن حيث الصنـع والمـواد مطابقـة للمواصفـات البريطانيـة ومن أجود الأنواع ، يكون هيكل اللوحة مصنوعاً من مقاطع 60439 Bsen Bs5486 Part1  من الفولاذ بسماكة لا تقل عن 2 ملم ومعالجاً ضد الصدأ والتآكل ومدهونة دهن حراري ، وتكون أغلفـة اللوحـات مزودة بأقفال ومفاتيـح وغير نافذة المـاء والغبار ذات درجـة حمايـة وتدعم اللوحةEpoxy  إما إذا كانت خارجة فبالإضافة للسابق يكون ذات درجة حماية   IP55  IP65  بزوايا حديد طولية وعرضية وتكون ذات درجة حماية مع تمييزها بالألوان الأحمر  BS159  تكون القضبان النحاسية فيها مطابقة للمواصفات البريطانية والأصفر والأزرق للفازات والأسود للحيادي والأخضر للأراضي ، كذلك يجب إن تكون هذه يكون قياس هذه القضبان مناسباً للحمل المطلوب وقادراً على تحمل القضبان معزولة بمادة PVC الاجهادات الميكانيكية والكهربائية الناتجة عن الأعطال وقصر الدائرة ، تكون اللوحة الرئيسية وشبه الرئيسية مزودة بأجهزة فولتيميتر واميتر لقياس الجهد والتيار المسحوب للفازات الثلاثة مع كافة ما يلزم من محولات تيار وجهد إذا لزم . وفيوزات ويجب أن تكون اللوحة الرئيسية مجهزة بمكان خاص لتركيب العداد حسب متطلبات شركة الكهرباء .

تحتوي اللوحات (الرئيسية وشبة الرئيسية ) على قواطع حرارية مغناطيسية من النوع المصبوب   من اجود الانواع وذات سعة مناسبة حسب ما هو مبين BS4752حسب المواصفات البريطانية

في المخططات محتوية على حماية ضد التيار الزائد ودائرة القصر .

تكون سعة القطع للقاطع الرئيسي 5 ك.أ ، و 35 ك.أ وسعة الباسبار لا تقل سعته عن 1.5 مرة من سعة القاطع الرئيسي .

إضافة إلى ذلك اللوحات شبه الرئيسية من النوع الذي يركب متساطح مع الجدار مع امكانية توصيل الكوابل له من الاعلى والاسفل .

لوحات التوزيع الفرعية :

تكون هذه اللوحات من حيث الصنع والمواد مطابقة للمواصفات البريطانية BS5486   و,  BSEN 60439  من أجود الأنواع ، وتكون معدنية غاطسة في الجدار ما لم يرد نصاً بذلك يكون هيكل اللوحة مصنوعاً من مقاطع الفولاذ بسماكة لا تقل عن 7. ملم ومعالجاً ضد الصدأ والتآكل ومدهونة دهان حراري ويكون باب اللوحة مزوداً بقفل ومفتاح وغير نافذ للماء والغبار ويكون قياسها مناسباً للأحمال مع تميزها بالألوان ومعزولة بمادة  PVC  ذات درجة حماية  IP40 تكون القضبان النحاسية العمومية فيها مطابقة للمواصفات البريطانية  المطلوبة والاجهادات الميكانيكية والكهربائية الناتجة عن دائرة القصر .

تحتوي هذه اللوحات على قاطع حماية رئيسي حراري مغناطيسي وقواطع حرارية مغناطيسية ومن أجود الأنواع وتكون سعة هذه القواطع حسب المواصفة البريطانية Bs3871  فرعيMCB حسب ما هو مبين في المخططات تكون سعة القطع للقواطع لا تقل عن 6 ك .أ. بحيث يمكن نزع أي قطع من اللوحة دون التأثير Plug-in يكون تركيب القواطع فيها بطريقة على توصيلات باقي القواطع فيها ، تكون اللوحة من النوع الذي يركب غاطس في الجدار مع إمكانية توصيل الكوابل والأسلاك لها من الأعلى والأسفل .

المفاتيح :

حسب المواصفة البريطانية BS 3676 و من أجود الأنواع .

الأباريز :

حسب المواصفة البريطانية BS 163  و من أجود الأنواع .

المواسير والعلب وتوابعها :

مواسير بلاستيكية صناعة محلية حسب المواصفة البريطانية BS4607 و من البلاستيك المقوى فئة (ب) .

PVC conduits heavy guage – class B

مواسير فولاذية مجلفنة حسب المواصفة البريطانية

BS31 Class B

الأسلاك :

ذات جهد600/1000 Volt

نحاسية مجدولة حسب المواصفة البريطانية BS6004

الكوابل :

نحاسية مجدولة وبالاقيسة المبينة في المخططات وجداول الكميات ذات جهد 600/1000 V

كوابل غير مسلحة PVC/PVC. حسب المواصفة البريطانية BS6004

كوابل مسلحة  PVC/SWA/PVC حسب المواصفة البريطانية

BS6004,BS5467,BS6121

كوابل مسلحةXLPE/SWA/PVC   حسب المواصفة البريطانيةْ BS6360

نهايات الكوابل Cable Shoes

من أجود الأنواع وحسب المواصفة البريطانية BS6121

قضبان التاريض  من  Copper-Clade Steel بقطر 20 ملم وطول 300 سم والى الحد الذي يؤمن النظام الأرضي المطلوب بحيث تكون مقاومة الأرضي الكلية لا تزيد عن 2 أوم .

وحدات الإنارة LED من أجود الأنواع وDRIVERS  وبموافقة المهندس المشرف ووحدات الإنارة الأخرى من أجود الأنواع وبموافقة المهندس المشرف .

تكون العلب المستعملة في مجمعات الهاتف والتلفزيون مطابقة للمواصفات البريطانية BS4662 أو الألمانية VDE0606 وتكون مصنوعة من مواد لا تساعد على  الاشتغال مثل الحديد المجلفن أو الـ PVC المقوى ومن أجود الأنواع .

كوابل التلفزيون : من أجود الأنواع .

كوابل الهاتف : مطابقة للمواصفات البريطانية  BS573وتكون مكونة من موصلات نحاسية مزدوجة بحيث يكون كل زوج مكون من موصلين ملويين حول بعضها البض صناعة محلية .

كوابل وأسلاك شبكة إنذار الحريق : مطابقة للمواصفات البريطانية   BS6207 Part1تكون الكوابل والأسلاك حسب توصية الشركة  الصانعة وموافقة الدفاع المدني .

على المقاول تقديم شهادات خاصة صادرة عن مختبر معتمد تثبت صلاحيته ومطابقة جميع الأجهزة المستعملة في شبكة إنذار الحريق للمواصفات المعتمدة ، إضافة إلى تقديم كتيب يحتوي على المعلومات والتعليمات الفنية الكاملة المتعلقة بتركيب وصيانة نظام الإنذار من الحريق بالإضافة إلى قائمة بقطع الغيار الموصى بحوزتها ، وكذلك موافقة الدفاع المدني على المخططات التنفيذية والأجهزة وتسليم النظام للدفاع المدني وان تكون الأجهزة من أجود الأنواع .

على المقاول أن يرفق مع عرضه نوعية ومواصفات المواد المنوي استخدامها في هذا العطاء والذي بني على أساسها أسعار بنود جداول الكميات مع مراعاة ما ورد في البند رقم (6) اعلاه .

ELECTRICAL WORKS

SPECIFICATIONS

Work under This Contract: -

The electrical installation covered under this division of the specifications shall include the supply and installation of the following: -

- DISTRIBUTION NETWORK SYSTEM:

  - Lighting Distribution Network.

  - Power socket outlet network .

  - Electrical fittings and accessories .

  - Earthing system .

- TELEPHONE INSTALLATION .

- Fire Alarm System.

- Computer Network .

- AUDIO & VIDEO SYSTEMS.

- Electrical Elevators .

- UPS

- Lightning System

- CCTV

    - DISTRIBUTION NETWORK SYSTEM:

  - Lighting Distribution Network:

Complete distribution network system for lighting and power from the service boxes, and terminals to all electrically operated equipment, including feeder and sub-feeder lines, distribution and sub-distribution panel boards, wiring and control equipment.

* The electrical power supply will be:

- 400 Volt between phases.

- 230 Volt between phases and Neutral.

- 50 Hz. (Cycle).

- Directly grounded Neutral.

  - Drawings: -

a. The Engineering Drawings issued with these specifications indicate the approximate location of all electrical apparatus.

b. The contractor shall check architectural, plumbing, heating and ventilation drawings to over come possible installation conflict. If some changes from the original plans be necessary to resolve such conflicts, the contractor shall secure the Engineer's approval, before any installation work is started.

c. Discrepancies shown on different drawings or between drawings and specifications shall be brought to the attention of the Engineer for a decision.

d. The contractor shall visit the site before submitting his price.

e. The contractor shall submit three prints of shop drawings of scale 1:100, and no equipment shall be ordered unless such drawings are fully reviewed and approved by the Engineer.

f. At Handing over, one tracing and three prints of scale 1:100 and two sets of compact disks (CD) compatible with A.CA.D14 software. As-Built Drawings" shall be submitted, complete with technical literature and instruction manuals.

  - Regulations & Tests:-

a. All work shall be installed in a neat and workmanlike manner, so as to be readily accessible for operation.

b. All components, and material supplied shall be manufactured in compliance with the appropriate standards: -

i.   National Electrical Codes.

ii. The British Standard Institution (B.S.)

iii. Other approved equipment Standards.

c.   Equipment's, spares and accessories to be delivered into the stores of the Employer.

d. All Electrical equipment shall be tested in operation for proper performance to the satisfaction of the Engineer.

e. Mugger Tests. Earth meter test, Insulation test, and Continuity tests, must be made after installation has been completed, and just before final placing in service, of the equipment.

f. The maintenance period for all electrical works should be for two years from the date of handing over and acceptance including spare parts needed.

g. The consultant has the right to increase, decrease and cancel the quantity of any item or any part of the item in the B.O.Q during the execution of the project works, according to the project needs.

h. All materials should be new and in accordance with the latest relevant approved standards and governing authorities and of the best quality obtainable (three types shall be submitted for approval). Materials of first class should be used provided that confirm the specifications and shall be accepted by the Engineer/ client.

i. The contractor should provide all necessary equipment and personnel required for checking, doing the required electrical tests and making any required adjustment for correction of any errors or omission. The cost of these tests should be included in the contract price.

j. Faulty installations which do not meet the requirements of this specification or do not perform satisfactorily shall be replaced or corrected to the satisfaction of the Engineer/client without any cost to the client.

k. Current and/or power rating of electrical equipment shall generally include safety margin of 10% based on worst condition to be met in service.

Maximum ambient temperature based on 40oC regardless installation is to be in air condition area or not.

Equipment rating should be based on the reference ambient temperature.

l. It is the contractor's responsibility to make sure that the electrical equipment are properly stored. Any defective equipment due to bad storage conditions should be replaced by new equipment without any cost to the client.

m. All tests should be carried out by the contractor in the presence of Engineer/client representatives.

n. The contractor should provide catalogues and/or samples for electrical materials to the Engineer for approval before ordering them.

  - Engineer and Workmen: -

The contractor shall have an experienced Electrical Engineer and good experienced technicians to proceed with the work

The client representative has the right to refuse: The Engineer and/or any of the technicians.

  - Conduit Installation: -

a. Conduit installation shall be carried out in heavy gauge P.V.C. conduit complying with B.S. 4607. Or according to latest B.S. or in galvanized Conduits Complying with B.S 4568 or according to latest B.S or similar standards.

b.   No. Conduit of less than 20mm inside diameter shall be used.

c. Where the conduits are buried in wall, ceiling or floor, P.V.C Conduits and accessories shall be used. For surface installation, galvanized conduits and accessories shall be used in location where they will be subjected to mechanical damage.

d. Throughout the electrical installation the loop-In system of iring shall be employed.

e. All draw-boxes and junction boxes shall be ample size to permit the cables being drawn in and out. At lighting and switch points, the conduit shall be terminated in a suitable box, provided with internal lugs, to permit back-plates or switch grids being attached to them, by metal threaded screws.

f. The position of draw-in boxes shall be arranged so that they will always be readily accessible and an adequate number of draw-in boxes shall be provided in a conduit run, to ensure that cables can be installed or removed without damage.

g. Efficient means shall be provided to seal-boxes and fittings, against the increase of dirt during the building construction.

h. Conduit shall be installed at least 150 mm clear of, and preferably above hot pipes (water or steam) and 50 mm clear of gas, water and any other services.

i. The ends of all conduit shall be carefully reamered, to remove all burrs or sharp edges on the inside.

j. All bends are to be made on site to suit building dimensions and not more than two right angle bends will be permitted, without the inter-position of draw box.

k. All conduits shall be swabbed through before wiring is commenced, and cables shall not be drawn into any section of the system until all conduit and draw boxes are fixed in position, and completed in all respects.

l. Conduits shall be run in a symmetrical manner and for surface runs shall be secured by distance saddles at intervals not exceeding 700 mm.

For surface conduit runs, conduit boxes shall be of the raised back pattern.

m. Where conduits cross expansion joints, expansion couplers shall be installed at the position of the expansion joint and at right angles to it.  An earth wire shall be installed between the nearest conduit boxes on each side of coupling.

n. Fill density of conduits and boxes should not exceed 40% .

o. Conduit bending should be well arranged and neatly done such that bent radius should not be less than 2.5 time the conduit external diameter.

p. Conduits running vertically should be firmly attached to the structure.

q. Minimum clearance between parallel running conduits should not be less than 3 times the largest running conduit diameter.

r. When the conduit is bent at least two clamps or saddles at least should be installed ( one at each bend end ) .

s. When connecting to the motors or recessed lighting fixtures last 600mm piece should be flexible and firmly fixed at both ends.

t.  Min. one fixing clamp or support should be provided for every 3 meters conduit length running vertically and minimum one clamp or support should be provided for every 5 meters conduit length running horizontally .

u. Complete co-ordination shall be made between electrical, mechanical and other contractors working in the project to run the installations of electrical and mechanical works over the reflected false ceilings and in shafts. ( Ducts ) . Drawings showing the routes for different services shall be submitted for approval before starting the work.

v.   Galvanized steel Conduits: -

Conduits and fittings shall be class 4 heavy protection both inside and outside welded steel, screwed hot-dip Zinc coated, sherardizing inside and outside

-All joints in the conduits shall be screwed.

-All conduits shall be free from rust patches or mechanical damage.

-All exposed threads, die marks and other abrasion shall be painted with tow coats of an approved metallic paint immediately after the conduit is installed.

-Conduit and conduit fittings shall comply with B.S 4568 or according to latest B.S or similar.

-Used for exposed electrical installations (surface mounted) or where necessary.

Note: -

All Electrical installation should be carried out by heavy gauge P.V.C. conduit and P.V.C. accessories according to B.S. 4607 for buried installation, but shall be carried out by heavy protection galvanized steel Conduits, for exposed electrical installations (surface mounted).

  - Conduit System for Special Services:-

Conduit installation for telephone, bell, and T.V. antenna, or other special services shall be carried out to the same standard as for power and lighting services.

Cables or draw wires shall be supplied and installed.

  - Separate Conduit Runs:-

There shall be a distance of at least 300 mm. between high voltage

(power, lighting and heating), conduit runs and low voltage (Telephone, Bell, T.V., Computer) conduit runs.

There shall also be a separate conduit run for each type of electrical installation (Power, light, telephone ... etc.).

  - Cable: -

a. All cables shall be of one manufacture only, and shall be delivered to site with the maker's seal, labels or other proof of origin intact.

b. All cables shall be color coded in accordance with the Jordan Regulations.

c. Cables shall be installed in one length from terminal point to terminal point. No through joints will be allowed unless specially specified by the Engineer.

d. Cable core identification color coding shall be employed throughout the installation and the following colors shall be used:-

PHASE A 		 :  RED

PHASE B 		 :  YELLOW

PHASE C 		 :  BLUE

NEUTRAL  		 :  BLACK

EARTH     		 :  GREEN OR YELLOW GREEN

e. All P.V.C. insulated cables multi core or single core shall be rated at 600/1000 volts and comply with B.S... 6004., or the latest B.S.

f. Cables shall not be drawn into conduits until work is completed, and permanently fixed.

f. All cables conductors shall be of electric copper type, stranded and PVC insulation.

g. Minimum conductor cross section area for cables and wires used for communication and signaling circuits should be 1mm2.

h. Minimum conductor cross section area for cables and wire used should be 2.5mm2 for lighting circuits and 4mm2 for power Sockets outlets .

i. All wires should not be cut, complete length from the equipment to the junction box be done without joint. Wherever the wire is cut it should be bolted in the equipment junction box.

j. All cables or wires which are connected in parallel should be of the same size and type.

k.Min. cable radius bent shall be 10 times the cable overall diameter.

l.Cable entries in to equipment shall be by cable glands ( Weather proof type and water tight ).

  - Bonding and Earthing: -

a. All conduit connections, switchboards, fittings, etc., shall be properly screwed together to ensure perfect mechanical and electrical continuity through out.

b. Great care is to be taken in bonding and earthing the installation and tests are to be carried out as the work progress to check the earth continuity of all metal work, conduits ... etc., and earth continuity conductors.

c. All exposed metal work, structural or otherwise, and all the metal work of any gas or water services, shall be bonded to the earthing termination of the intake position in according with IEE Regulations.

d. No earth continuity conductors shall be less than 2.5. mm2 tinned copper cable insulated and colored green.

e. The frames of all electric motors and starting panels, etc., are to be efficiently "earthed"

f. Number of earthing electrodes required could be increased to maintain earthing resistivity less than 2 ohm .

  - For external lightings :-

The work shall be carried out according  to drawings and  Engineer instructions. The external lighting distribution board shall be installed as shown in External lights drawing which are equipped with main and branch MCB’s. Contactor and timer with automatic push buttons.	Buried under ground PVC/SWA/PVC armored cables  of the  sizes and routes shown  in drawings , shall be installed from the  external distribution board to external lighting fixtures shown in drawing .. The cables shall run in suitable conduits before entering or leaving the lighting fixtures , while the rest of the cable shall be buried underground . When using PVC/PVC cables , they shall run in galvanized  conduit  if they are surface mounted , specially when they run on walls and external surfaces .

The external lighting points will consist of conduits , water proof boxes, under ground cables , and all civil works needed to complete the work in good order . The external lighting points can be underground cables or cables in PVC conduits (buried ) or cables in galvanized conduits ( Surface mounted ) including all necessary accessories needed for the external lighting purposes .

  - Lighting Switches and socket outlets :-

a. All lighting switches shall comply with B.S. 3676 or the latest B.S. and shall be of the rating specified on way, two ways, or other type as required. Where grouped together and connected to the same phase, they shall be mounted in a multi-gang box with common cover plate, where grouped together and connected to different phases.  Phase barrier switch boxes with common cover plate and secondary cover plate having a suitable warning inscription shall be used.

b. Switch shall be of the AC ONLY type (10 Amp. rating), enclosed in metal clad boxes and suitable for surface or flush mounting as required. Switches shall be of the weatherproof pattern for exterior situations.

c. Flush mounted switches shall have a grid assembly.  One and Two gang switch-plates shall be mounted on a gang box. Three and four gang switch-plates shall be mounted on a two-gang box.

d. 13 Ampere 3 Pin socket outlets with switch shall be of the fused pattern incorporating a robust shutter mechanism operated by the earth pin on insertion or withdrawal of the plug.  The sockets and boxes shall comply with B.S. 1363 and B.S. 4662 respectively.

e. All 13 Ampere 3 Pin socket outlets with switch shall be complete with a fused plug top, and weatherproof 13-ampere switch socket - outlets shall be complete with the fused top entry plug.

f. All outlet box feeding fixed equipment such as fans, pumps, boilers, air handlers. ... Etc., shall be equipped with a switch fuse rate, as shown on the drawings and shall be of the same series of the conduits and shall have the same protective coatings.  They shall be provided with suitable covers, and shall have enough openings of the proper size for the introduction and securing of conduits, they shall comply with the standards requirements

g. Stabilized socket outlets for computer use shall be  twin 13 Amp, 3pin socket outlets with switches and indication lamps. According to drawings and Engineer instructions, and shall comply with BS-1363 .

h. Industrial power socket outlets of single outlet, 3P + N + E, 3-phase, polarized, earthing type, rated 32 A, 380/415 V. The industrial sockets shall be manufactured in accordance with B.S 4343, BSEN-60309-2 and IEC-309-2, corrosion and impact resistant, sealed against water and dust, with splash proof box and hinged spring – return plate, complete with matching plug of same material.

i. All socket outlets shall be provided with plugs of the same types and manufacturers .

j. Sockets installed outdoor or in places subjected to dust or vapour should be of weather proof type and mechanically rigid .

General:

- Manufactured within a BS5750.

- Carpet trim and lid tray molded from top quality “Nylon 66”.

- Carpet trim reinforced with steel for increased strength.

- Strong lid tray hinge design ensures reliable lid operation.

- Lid tray comprises 3 mm galvanized steel housed in a moulded tray thus insulating the steel, avoiding earthing leads.

- Strong design for lid lifting handle allows frequent use without failure.

All wirings shall be in PVC conduits buried in floor under tiles, installed from distribution Boards, or data Boxes to access floor boxes as shown in drawings and according to engineer’s instructions.

Three types shall be submitted for approval.

1.12.    Feeders and Sub-Feeder Installations: -

a. Feeders and sub-feeder lines to distribution panel boards or to motor control centers shall be either single (P.V.C.) wires inside conduits or multi-core cables run exposed in trenches, or cable shafts.

b. Where exposed cables are liable to mechanical damage or running through location with flammable materials, they shall be inside conduits or in enclosed cable trenches as required by the Engineer.

c. No joint or splices shall be accepted on main or sub-feeder lines.

d. The cables shall not be buried directly under the concrete or under the floor tiles.

e. The contractor shall take special care wile installing and commissioning electrical installations in such a way not to spoil other services.

f. Multicore cables shall be of PVC insulation .

g- Installation of Underground cables:

The under ground cables shall be laid in trenches not less than 75cm below the ground level. The sides of trenches shall be trimmed neatly and the bottom shall be leveled and smoothed. The width of trenches shall not be less than 40 cm. After the cables are laid, the trenches shall be backfilled to a depth of 15cm with fine selected soil free from lumps, metallic or other foreign inclusions or, where required by Engineer, by washed sand and bricks. The remainder of the trench shall be backfilled in an approved manner with soil, which shall be rammed down and thoroughly consolidated.

Where two or three cables are laid in one trench, the cables shall be pulled straight and spaced not less 15 cm (center line to center line).

Where the cables cross the asphalt or concrete roads and enter into buildings they should pass through heavy duty (heavy gauge) PVC pipes covered with concrete as indicated on the drawings. The ducts should extend one meter beyond the kerb line of the road in either side.

The proposed routes of cables are shown on the layout drawings. The contractor should check location of other services and shall submit final cable routes drawings for approval of the electrical and site Engineers before commencement of any cable layout work.

Where under ground cables are required, all the above civil works shall be included with the price of cables.

1.13.    Main Distribution Board: - (MDB):-

This contract calls for the supply and installation of an indoor type switch- board assembly, which should be suitable for operation at 230/400 Volt, 3 phase, 4 wire, 50 Hz. MDB should be factory assembled and tested in according with the latest applicable regulations MDB shall be :-

- Free standing panel, or cubicle type, dust proof, made of rigid steel sheet.

Anticorrosion on zing coated, lead chromate coat then primary and secondary of heat treated paint ( paint should be scratch resistant and be easily repaired ).

- Internal wiring should be neatly done and well arranged and wires are properly fixed by clamps and double nuts .

- Single line diagram should be attached to the main D.B to show all cables, circuit breakers, switches incoming or outgoing form the board.

- All feeders should be identified by number and described by the load served

- Copper Bus bars should be of rectangular cross section, and neutral bus bar should be provided as well as earthing bus bar .

- Busses and incoming cables should be marked clearly to identify the bus bars by colored plastic discs to show ( Red. Yellow. Blue. Neutral. Earth ) or by plastic sleeving

- All C.B to C.B connection should be done by copper bus bars strips and not by clables .

- Tumbler lock should be provided with a master key for all distribution boards

- Operating handle of breakers should show clearly whether breaker is on open.

- MCCB should be of quick make, quick brake, trip free type .

- Panel should be installed on level embedded steel channel ( at grade it shall be installed on 100mm high pads . and should be equipped with the following: -

a. Air Circuit Breakers:

The Air Circuit Breakers shall be fully with drawable type designed to comply with BS.4752 and/or IECI, and have a proven short circuit performance as 65 KA RMS.

The Air Circuit Breaker shall be designed as a completely self-contained cassetted unit which can be mounted in an LT panel compartment without additional screening. Safe access for routine maintenance shall be provided by lockable automatic safety shutters within the cassette.

A motorized operating mechanism shall be provided of the trip free type to enable the facility of slown closing to allow checking of operation and adjustment.

A front operated racking mechanism shall withdraw the AVB. The racking mechanism is still engaged in the isolated position which allows testing of control circuits. Further racking releases the ACB and the breaker can be withdrawn for inspection. A flag indicator will show the breaker position.

Mechanical Interlocks shall prevent the following:

The ACB being isolated unless it is in the off position.

The ACB being racked into the service position unless it is in the off position.

The ACB being accidentally pulled off the guide rail.

The ACB being slow closed in the service position.

Access to the racking mechanism unless the ACB is in the off position.

Each Air Circuit Breaker shall incorporate a microprocessor based sensing protection/information unit. The unit shall be adjustable for long time delay, short time delay, instantaneous trip and earth fault.

The typical setting ranges shall be:

Long time 	0.5 to 1.0	Nominal current rating

Short time 	1.5 to 8.0	Nominal current rating and flat

Long time 	0.5 to 1.0	Nominal current rating

Short time	1.5 to 8.0	Nominal current rating and flat

Response characteristics and definite minimum time delay

The unit shall have a display which shall be capable of indicating phase and earth currents, present power demand (Watts), Peak demand (Watts) and energy usage (Watt Hours).

Following a trip the unit shall be capable of displaying the cause of the trip and the current at the time of trip.

b. Branch moulded case circuit breakers with interrupting capacities as follow: -

1.  Up to 100 A rating   	:  25 KA

2.  125 A to 250 A rating	:  35 KA

3.  300 A to 800 A rating	:  50 KA

c.  MDB should consist of a completely enclosed, free standing metal structure with frames and insulating blocks to support and brace all main buses to withstand an available circuit current of at least 60 KA RMS symmetrical at 400 Volts. Metal structure used of 2 mm thickness.

d.  All main busbars and bus connections to breakers, should consist of electrical grade copper of a sufficient size of at least 25% higher than main circuit breaker frame size, and braced for a symmetrical rms short circuit duty equal to or higher than main circuit breaker interrupting duty, for minimum of one second to limit temperature rise 50 deg. cent. over and average ambient temperature outside the enclosure of 40 deg. cent. Bus-bar will be based on maximum of 1.55 Amp. Per Square millimeter of cross sectional area .

e. A laminated plastic nameplate engraved with white characters on a black background shall be furnished for each device on the MDB.

f. Installation Fiber to be used above all MCCB'S and below the metallic sheet cover above the MCCB'S.

g.   Microprocessor Based Metering Package:

1. General

This specification deseribe the requirements for a digital line metering and protection system to be provided on the front of each incoming section. The device shall consist of a single microprocessor based unit capable of monitoring and displaying the function listed below. The device shall provide the protection functions indicated and the capability to communicated data via network.

2. Monitoring Functions

Microprocessor based monitoring unit shall be installed adjacent to each ACB as indicated. The unit shall have a single LED display selectable for the following indication:

a) Line Voltage (V) 		1% 	accuracy

b) Phase Voltage (V) 		1% 	accuracy

c) Current (A) 			1% 	accuracy

d) Power (W) 			2% 	accuracy

e) Reactive Power (Var) 	2% 	accuracy

f) Power Factor 	 4% 	accuracy

g) Maximum Demand (W)        2%       accuracy

h) Frequency (HZ)                    0.5%    accuracy

The unit shall have the capability to interface with the Building Management system to provide the information in (a) to (h) through an interface to a remote location. In shall also allow control through the same system.

The unit shall be capable of detecting and providing an output for voltage and current phase loss/phase unbalance, reversal, over voltage and under voltage. All parameters shall be user adjustable.

3. Protective Functions

The device shall trip and/ or alarm on the following conditions as indicated:

Voltage phase loss, if any phase rms is less than 50% of the nominal line voltage.

Curent phase loss, if the smallest phase valuve is less thatn 1/16 of the largest phase value.

Line voltage phase unbalance, selectable from 5 to 40% in 5% increments.

Voltage phase reversal.

Over voltage selectable from 105 to 140% in 5% increments.

Under voltage, selectable from 95 to 60% in 5 % increments.

The device shall have a time delay for the strip and / or alarm settings for over voltage,. Under voltage and phase unbalance. The delay shall range from range from 0 to 8 seconds in 1 second interals.

4. Inputs

Input ranges of the device shall accommodate external curent transformers with ranges from 100/5 through 5000/5. potential transformers shall not be necessary up to 600 volts.

5. Outputs

Outputs shall have trip / alarm contacts with ratings of 10 amperes resistive.

6. Display Screen

Display and LED's shall indicate both trip and alarm conditions. The cause of a trip or alarm shall be indicated on the negative power factor, and negative KVAR. The unit shall trip in the event of an internal malfunction.

7. Operating Characteristics

Control power shall be drawn from the monitored incoming AC line terminal connection.

The device shall have non-Volatile Memory and not require battery backup. In the event of a power failure, the device shall retain present parameters.

The device shall allow user to disable undesired values/functions and to later reactivate them if required.

A neutral terminal shall be provided for 4 wire , grounded systems.

The Voltage Power Module shall be detachable from the chassis.

In the event of a trip or alarm condition, a built-in reset button shall allown a manual reset of the device. The device shall also be capable of being remotely reset via its communication part.

8. Data Communication

Supply for an addressable communication card capable of transmitting all data, including trip data, over a local area network to a central computer for storage and / or printout.

h. Installation of three Ammeters and one voltmeter with S/S (Selector Switch).

-	The SMDB's - Sub main Distribution Boards MCC – Motor control center….etc should have the same specifications of MDB as mentioned above according to drawings.

-	All (MCCB)-Moulded case circuit breakers in MCC , Main, and Sub-main Distribution Boards etc … shall be of adjustable type.

i. The contractor shall submit three copies of schematic drawings of MDB to the Engineer for approval before manufacturing and installing boards, showing ratings, rupturing capacity of all breakers, size and dimensions of bus bars, Dimensions of Boards and thickness of all metallic sheets, paintings, . . . etc.

j. Main Electrical distribution board shall be manufactured and installed in accordance with Electrical Distribution Company regulations and specifications where the project is belonged.

1.14.    Distribution Boards :-

Distribution panel boards for lighting, socket outlets and other appliances should be totally enclosed in a robust sheet construction stove enameled and arranged for recessed or surface mounting. The panels have to contain main isolating switch and miniature (quick) circuit breakers (MCB's) plug-in type of rating and number as shown on the drawings.

Adequate bus-bars of appropriate current capacity, which should be at least equal to the rating of the protective device, through which the particular panel is fed. An insulated neutral bar should be provided with a sufficient number of ways to ensure that the neutral conductor of every circuit will be connected to a separate way.  The ground terminal bar should be securely fixed to the cabinet and having a sufficient number of ways to connect all ground conductors.

Single pole MCB's should be at least 60 Amps frame size with trip rating as indicated on the drawings, and having interrupting capacity at least 6000 A, 3 Pole miniature circuit breakers should have an internal common trip to prevent phasing.  All MCB's should be equipped with thermal and magnetic trip devices for overload and short circuit protection and should comply with B.S. 3871 part 1.No. MCB's of more than 60 Amps rating should be used.

For larger ratings moulded case circuit breakers of 22 KA minimum interrupting capacity should be used.

All wires in the boards should be numbered with special numbered rings, either phases or neutrals. list of all circuits shall be attached on all DBs

Earth leakage circuit breaker of suitable trip rating (0.03) A or (0.3) Amp. should be installed in distribution boards where needed  as shown in drawings.

Maximum Number of PVC insulated Standard Copper Cables through the Conducts

Nominal Conduct or size mm2	20 mm

or  "

25 mm or 1"	32 mm or

"

38 mm or

"
1.5	8	18	20	-

2.5	5	11	17	-

4.0	4	8	13	-

6.0	3	6	10	-

10.0	2	4	6	-

16.0	-	3	4	5

25.0	-	-	3	5

35.0	-	-	2	3

50.0	-	-	2	3

1.15.    Earthing System:-

General:-

The earthing system shall be in full compliance with the requirements of the "Regulations" and these specifications.

Unless otherwise specified all equipment used for earthing shall be of copper or approved copper alloys materials, and shall be specially manufactured for the purpose.

Equipment earthing shall consist of connecting all non-current carrying metal parts of the wiring system to earth source.

Earthing Rods:-

- Earthing rods shall be of the steel core copper jacketed type in one continuous length.

- Earthing rods top shall be permanently accessible through a covered access pit, as shown on the drawings.

- Earthing rods shall be made of high strength steel alloy core with a molten welded copper covering, and shall have a conical point and be chamfered at top to prevent mushrooming during driving.

Earthing Connectors:-

- Earthing connectors for connecting cable to pipe shall be split coupling bolted pressure type.

- Body of clamp shall be cast of high copper alloy provided with four durum or verdure oval shank bolts nuts and lock washers for connections. Cable shall be fastened to connector with double U-bolts.

- Earth pit with suitable cover should me made.

Earthing Of Panel Boards:-

- Panel boards shall be earthed by connecting an earthing conductor from the main rods to the cabinet and earthing bushings on the incoming and outgoing feeder to conduits, which should be according to B.S and Jordanian Standards.

- Panel boards which are interconnected by conduits shall be earthing by connecting the earth connector to the cabinet to earthing bushings or the incoming feeder conduits.

- Earthing bushings shall be as specified in the sub-division “Conduit and Fittings ".

Earthing of Receptacles:-

All receptacles shall be earthed by connecting a conductor from the receptacle earthing terminal to earthing bushings on the incoming.

1.16 Metallic Cable Truncking:-

Steel cable trunking shall be made of painted Zinc coated steel. It shall have inward flanges on the body for strengthening and it is complete with easily fitted covers, which are locked in place and fixed to the body by suitable screws.

Standard trunking accessories such as Tees, angle tees, four way through boxes, offsets.. etc. shall be used. These accessories shall be made by the same steel trunking manufacturer and included in the price of truncking. Each length of cable truncking and accessories shall comply with BS2989 and BS4678 or equivalent standard.

When PVC truncking is required, it shall be of PVC conduits specifications.

1.17.    Cable Tray:-

a. Cable tray shall be provided as indicated or required for the proper installation of the cables.

b. Trays and its accessories shall be made of heavy gauge perforated sheet steel, hotdip galvanized, of thickness … not less than 1.5 mm.

c. Trays shall be fixed to the supporting structure by approved suspension rods or steel angle brackets at distances not exceeding 1 meter.

d. Tray fill density should not be more than 40%.

e. Perforated cable trays are not allowed to be used for communication, sound system, and fire alarm system cables.

f. Trays should be covered by steel hot dip galvanized covers fastened according to the manufacturer recommendation and to be included in cable trays price.

g. Cables running on trays should be firmly clamped (Every 2 meters for vertical run, and every 5 meters for horizontal run) .

h. Tees, angle tees, offset fittings should be factory fabricated by the same manufacturer of the cable trays.

1.18.   Motor Control Center:-

The motor control centers shall be bolted and shall be made by the same manufacturer as the main distribution board.

MCC shall be suitable for operation at 400/230V, 50 Hz , 3-phase, 4 wires system and solidly earthed .

Motor starter shall be thermal magnetic type with overload, under voltage and phase failure protection. The panel shall contain the necessary contactors, over load relays, inter locking, current limiting and pilot lamps for each motor and for the main supply.

The starter shall be equipped with start-stop push button and indicating lamps.

Direct on line starters are allowed only for motors less than 2 KW, starting current reduction starters for motors above 2 KW should be provided .

All Breakers in MCC shall be MCCB ( Moulded case circuit breaker ) and MCB ( miniature circuit breaker) as shown in drawings.

MCC shall consist of the required branch circuits with 20% ( min one for each size and type ) installed spare circuits .

Every component in the motor control center should be named by engraved plastic. Schematic diagram should be supplied with the MCC. Metallic sheets should be 2mm thickness for the MCC.

MCC shall be installed as shown in drawings .

Prior to installation , the contractor shall submit to the engineer for approval the wiring diagram of the installation for MCC and the suggested layout of components . MCC shall have its wiring diagram attached and fixed on the inner side of its cover .

Breakers of MCC shall be of same manufacturer of MDB.

Contactors, over loads and other devises of Telemecanique made  .

2- TELEPHONE INSTALLATION

2.1.1.     General :-

The telephone installation distribution network shall be arranged as indicated on the drawings. The system shall be fully separated from other systems .

2.1.2.     Standards :-

Telephone installations are to comply with the requirements of Jordanian TRC (Tele-communication Regulatory Commission) and the relevant CCITT ( The International Telephone and Telegraph Consultative Committee) recommendations .

2.1.3.     Telephone Wiring :-

a.  Multi-pair cables for indoor installation between MDF and the terminal in the floors.  The wires should be 0.6 mm.

b. Two pair cables should be P.V.C. insulated and P.V.C. sheathed. The wires should be 0.6 mm minimum .

2.1.4.     Telephone Terminal :-

a.  Telephone terminal cabinet shall be sheet metal enclosure, surface or flush mounted, and should be approved by the engineer.

b.  Cabinets shall enclose the necessary terminal blocks for terminating and tapping telephone cables.

c.  Every telephone terminal to have a number.  The same number should be in the associated telephone box. Using numbered rings on wires.

d.  Every telephone socket outlet to have its top entry plug and of same type and same manufacturer or shall be (RJ 11) type as required.

3- FIRE ALARM AND DETECTION SYSTEMS

3.1.     Purpose :-

1. Detect automatically the presence of fire and give local audible warning.

- Provide audible warning upon the manual operation of a call point.

3.2.     Design Standards :-

The system should be installed and maintained in accordance with the recommendations of the British Standard B.S. Standard" Code of Practice Installation and Servicing of Electrical Fire Alarm System", or comply with equivalent approved international standards and in accordance with any local regulations relating to Fire Alarm and fighting System.

3.3.     Extent of the Works :-

This section of the specification covers all the work associated with the installation of a fire alarm system of the manual type and all associated equipment.

The works include the supply, installation, testing and commissioning and the delivery, clean and in working order, of the system shown on the drawings and specified in the specifications including all details such as :-

a.  Fire Alarm Master Indicator Panel complete with supervisory extension buzzer, battery and charger unit, all internal wiring ... etc.

b.  Fire alarm push buttons, and alarm bells ( gongs ).

c. All wiring, conduits, labour, tools, instruments scaffolding ... etc., necessary to execute the system in a first class manner, even such labour and materials are not specially mentioned but are necessary for a satisfactory completion of the works.

d. Supply of complete operation manual as specified as well as instructions to the Employer's operation personal.

e. The contractor must obtain the approval of local civil Defense  Authority for fire fighting and fire alarm systems- or other authorities required by the law, on all equipments, materials used, workshop drawings , before carrying on the  installations of the systems and before starting the works . Also at the end of project works (Handing over time).

3.4.    Wiring :-

Fire alarm wiring shall be completely segregated from any other system.

All internal wiring between bells, push buttons, and detectors to fire alarm control panel (FACP), shall be 1.5mm2 and between bells and fire alarm conrol panel (FACP) shall be 2.5mm2.

The interior wiring shall generally be concealed in embeded PVC conduits in accordance with the specifications for electrical installations.

No fire alarm wires or cables are permitted to be exposed .

3.5.    General Description of Operation :-

a.  The fire alarm system shall  protect risk area within the premises by giving warning of the fire condition when detected by an automatic detector or by the operation of the break glass call. The system shall be maintained in according with B.S. 5839 or comply with equivalent approved international standards.

The risk area divided into zones, and each zone have it's own fire indicator on the Control Unit.  the location of an alarm can thus be determined at the Control Unit.  Operation of an individual detector shall be displayed by an indicator fitted into the base or body of the detector.  This indicator shall illuminate when the detector goes into alarm.

Upon receipt of an alarm, the Control Unit shall perform the following actions :-

(1)  Illuminate Fire Zone Indicator.

(2)  Activate Alarm Warning Devices within building

(3)  Operate Internal and External Fire Sounders .

(4) Operate Ancillary Devices as appropriate, such as switching off MCC , Chillers, Fan coil units and lifts, doors, holder system, sprinklers, flows swithches and switching on exhaust fans.

b.        Fire  Alarm Control Panel ( FACP ) :-

The control panels shall be of solid state component and comply with B.S 5839 - PT-1 or with equivalent approved international standards, and shall be as follow :

A- Fire Alarm control Panel (FACP) 16  zones of a modular design, as shown in drawings, and include the followings :-

- 12 way detection zone modules, with zonal outputs  rated at 100 ma.  On board selectable auto/test feature  On board selectable delayed response.

- Integral battery charger of 5 Amp D.C. rated from a supply of 240 V A.C. or 100 V A.C. at 50/60 Hz.

- All circuits monitored for fault conditions.

- Choice of sounder output mode of test, continuous or pulsed. Twin monitored sounder outputs.

- Internal buzzer.

- The facility to extend the detection capability

- The cabinet trim and door assembly shall have an allen screw fixing to prevent unauthorized entry

- English/Arabic legend available as standard.

- Annunciate .

- test switch .

- silencing switch .

- visual indication .

- Operating temperature range-10 Degrees Centigrade to +55 Degrees Centigrade.

- Humidity - to 95% condensing.

- The battery shall have a capacity to sustain the system for 24 hours, and alarm for one hour .

- 20% spare circuits should be included in the fire alarm panel .

- Every zone should be tagged and designated by description to indicate ( ex. 1st floor north – west ).

c.        Manual Alarm Call point :-

A surface or flush mounting manual clapping meeting the requirements of B.S. 5839 : part 2 or approved international standards. The unit contains a key operated test facility and the glass in plastic coated to eliminate loss fragments, so the glass should not be broken and can be used again without any damage Protection to IP44. It should be painted red with the wording “Fire” in English and Arabic .

d.  150 MM Alarm Bell :-

A 150 mm diameter continuous ring alarm bell with a sound output of 91 dB (A) at 1 meter . 24 Vol. DC operation with an IP rating of IP 20 and if used with weatherproof gasket box IP 44, Red colour .

e. Photo-OPTICAL Smoke Detector :-

Shall be of the optical light scatter type with encapsulated electronics meeting B.S. 5446 Part-1 or approved international standards. The sensing element should be fully shielded against ambient light and should utilize a symmetry sampling cham to give an even sensitivity about the detector axis.

f.   Heat Detector :-

Shall be of the combined rate of rise and fixed temperature type.  The detector shall be solid state meeting B.S. 5445 Part-5 or approved international standards.

The rate of rise temperature detector shall be calibrated to respond to an increase in ambient temperature of 3 C. degrees per minute.

The fixed temperature detector shall be set at 58 C. degrees.

Testing facility should be provided to test the detectors operation .

g.   Detector Bases :-

To allow for complete flexibility, the above detectors will utilize interchangeable bases which incorporate a LED response indicator.

i. Remote lamp indicator :

Lamp indicators shall comprise an xenon flashing indicator housed within red lens. They are mounted in places where noise would prevent the sound being heard or in some important places as shown in drawings .

j. End of line device :

Exact value and characteristics of end- of – line device shall be determined, supplied and installed accordingly . Equipment is to operate without manual adjustment and without falts or false alarm .

k. Flashing lamp unit :

Xenon flashing lamp units, suitable for use in areas of high ambient noise levels or where deaf personnel are present, 24 V nominal voltage DC., 63 flash rate per minute, 20-30 V DC working voltage with power output not less than 5 watts.

l. Testing facility should be provided to test the detectors operation .

m. Tests for fire alarm system are to be done as follows :-

-   F.A system components shall be tested, calibrated after installation in accordance with the manufacturers standard practice .

-   Wiring continuity, short circuits and earthing should be tested .

-  Satisfactory operation .

n. Spare parts list .

3.6.    Spare Parts :-

The contractor shall also submit with his tender guarantee that will hold a sufficient number of spare parts for the maintenance of equipment ... etc., A list of such spare parts shall be submitted to the Engineer for approval before the completion of the system.

3.7.    Contractual Maintenance Period

The contractor shall maintain the system and all associated equipment of all descriptions for a period of Two years , from the date of handing over to the Employer.

Any item of material found to be defective, shall be replaced by the contractor, within seven days of his being notified, and any results of defective workmanship shall be repaired including supply of new parts if necessary, immediately upon being notified.

In his tender, the contractor shall allow for the cost of this maintenance and inspection service including all tools, instruments, scaffolding, and the transportation thereof, as required for to correct and full execution of these obligations, and the provision, use or installation of all materials and parts which are faulty for any reason what so ever, excepting always ; Acts of Nature, such as storm, tempest or flood, lighting and earthquake, and civil revolt acts of war and vandalism.

The contractor shall be held responsible for, and shall make good, all defects in materials and workmanship, that appear during the Two years maintenance period.

The period of liability shall not end until all defects which appear during the maintenance period have been rectified.

During the maintenance period, the contractor shall carry out all necessary adjustments, repairs, cleaning, ... etc.

The contractor shall remove the whole of the system and re-install a new similar one if an unsolvable problem occurred in the system.

4 - COMPUTER  NETWORK SYSTEM

4.1.   Data Outlets   :-

Cat-6a- UTP cables in P.V.C rigid conduits of 1” diam, complete with boxes and then to be connected and installed on trunkings above tiles ceilings on corridors or were  needed  complete with and all needed accessories, to be installed for every data outlet from the patch panel to the data outlets in offices, halls or where needed according to drawings.  Data outlet should be provided with RJ45 face plate. The work shall be supplied, installed, connected as shown in drawings and specifications and to be tested.

By approved test equipment Patch Panels shall be mounted at suitable height and be mounted in communication cabinets (CC) in floors.

Patch Panels (PP) in floors shall be connected to main panel in server room by using  Fiber optics cables, PVC conduits of 50mm diameter (Trunks installed above false ceiling as per drawings ) (shop drawings shall be submitted before starting the work showing routs and all necessary details for approval).

Wiring and commission of computer network system shall be done by contractor.

-  All data outelets shall be numbered and labeled from both ends.

-  Structured Cable:-  Cable to be used in computer network are unshielded twisted pair (UTP) category “6A”  4 pair, Compliant with TIA/EIA-568-B.2-1, and shall be installed and connected directly from data outlets to patch panel cabinet in floors as shown in drawings.

Cable between Network Cabients must be shielded twisted pair (STP) category “6A”  4 pair, Compliant with TIA/EIA-568-B.2-1, and shall be installed and connected directly from Main data cabinet to other cabinets in floors as shown in drawings.

-  Face plates:-  Computer outlets face plates support more than on snab in part for the connector modules of RJ 45 for computers.

4.2  - Communication Cabinet:

It is a Wall-Mounted Communication Cabinet. It shall be installed & mounted in at 2.2 mt. from finish floor level.

Component 	Specification

Dimension 	Width 	Standard 19” EIA

Height 	≥ 9 U for cabinet in floors , 30U for Main Data Cabient.

Door 	Type 	Glass or Plexi

Power distribution strip 	≥ 4 MK Socket, Mounted into the cabinet.

Security 	Key lock

Cooling 	≥ 4” Fans (2 Nos.)

Warranty 	2 Years, Parts & Labor (On- Site)

4.3. Patch panel:

•  24 Port category 6A UTP

•  Should be mounted into the Communications Cabinet.

Metal Frame:

•  Aluminum

•  Three cut outs to accommodate 8 ports each

Front Bezel:

• 3 bezels of 8 ports each

•  High impact FR grade ABS

Note:-Contractors shall have to:-

•  Label both ends of each cable.

•  Use cable ties (not tape) to keep cables in the same location together.

•  Stay atleast 1m away from fluorescent light and other source of electrical interference.

•  Lacing of patch panel should be accordance with best international standards, such that no strains of cables behind or inside the cabinet.

•  From patch panel side, cable length should be adequate for easily and tidely connections.

Tests:

Testing of computer network should include but not limited to the following:-

a- Network mapping, attenuation of all cables.

b- Resistance and connectivity (pass or fail).

c- To determine (test) length of cables.

d- Print out of the results.

5-.  AUDIO & VIDEO SYSTEMS: -

The contractor shall supply, install, connect, commission and maintain audio , and video systems as shown in drawings and consisting of the followings:

Sound System for boardcast & Multipurpose area

It consists of the followings:-

5.1a  HORN SPEAKER

Shall be at least as follow

- Made from pure aluminum high quality

- Rated power 30 w

- Frequency response (85-1600 Hz)

- Max sound 100 db

5.1.c Amplifier

- 2+2 Input amplifier

- 180W AC for Boardcast / 150W AC for Multipurpose

- 3 mic/line

- Phantom power

- VOX active

- Priority

- With wall mounting tray

- Volume Controller

- 40W/ 100V transformer attenuator

- To fit 7x7 cm wall box

5.3 -Cable

5.31 .a Speaker Cable

-  Speaker Cable 1×1.5sqmm

-  Two insulated conductors and a common insulating coat on the outside.

-  O.D.: 9.20 mm

-  Weight: 14.30Kg/100 m

-  Operation. Temperature : - 5°C /+70°C

Jacket:

-  Material: PVC flame retardant

-  Normal. Thick.: 1.00 mm

Conductor:

-  D.C.R. [ ohm/km ] at 20°C:8

-  Conductor : 2x80x0.2

-  Delect. O.D.: 1.5 mm2/14

-  Area/AWG:1.5 mm2 /14

-  Insul. O.D.:3.4

-  Material: Bare copper fire resistant PVC insulated

5.3.b Audio Cable

-  Cable 2.7mm Foil Screen

-  Aluminium /mylar foil shield cable.

-  Extremely small outer diameter.

-  D.C.R. at 20°C : 65 ohm/km for Conductor

-  D.C.R. at 20°C :260 ohm/km for shield

Capacitance:

-  CDR/CDR 1 KHz : 100 pF/m

-  CDR/SCR 1 KHz: 300 pF/m

-  Nominal Impedance 1 KHz: 600 ohm/100 m

-  Attenuance 1 KHz: 0.5 db/100 m

-  Nduttance: < 58 μH/100 m

Cable:

-  O.D.: 3.10 mm

-  Weight: 1.40 Kg/100 m

-  Operating temperature: -35° C/+

Jacket:

-  Material:PVC

-  Nom. Thick.: 0.30 mm

Shield:

-  Material: Alumynium/polyester tape

-  Coverage:100%

Conductor:

-  Qty: 2

-  Strand : 7 x 0.20 mm

-  Area/AWG: 0.22 mm2/24

-  Insul. O.D.:1.00 mm

-  Material: Bare copper polyethylene insulated

5-4  MICROPHONE :

Shall be at least as follow

A-  Cardioids mic

-  Impedance       600 ohm

-  Frequency        500/15000  hz

-  Sensitivity        2.5 mV/pa

-  Length of cable  5m

-  Plug                    XLR

B-  FOR stand with telescopic rod

•  Impedance       500 ohm

•  Frequency        500/15000  hz

•  Sensitivity        2 mV/pa

•  Length of cable  5m

•  Plug                    XLR

C-  FOR WIRELESS mic

-  Including the UHF receiver

-  Range operate (798 to 826 Mhz)

-  144 selectable channel

-  Battery charger

-  Pll technology

6- ceiling Mounted Speaker

Full range wall mounted made of plastic material with front metal grille:

• Sensitivity 1W/1m : 90 dB

• Max.SPL/1m : 97 dB

• Frequency response : 100-15000Hz

• Rated Power : 15 W

• Dispersion angle @2KHz : 120 deg.

6.  -  ELECTRICAL ELEVATORS :

1.  GENERAL

1.1   The contractor shall give an evidence  and demonstrate  to the satisfaction of the owner / engineer that the manufacturer has an engineering organization immediately available in Jordan who can be called upon for advice and assistance as may be required and that there is representation in Jordan that can immediately satisfy necessary spare parts to support day – to – day maintenance requirements .

1.2   The contractor’s superintendent shall give competent instructions for the operation and maintenance requirements which shall be submitted . this however, shall not relieve the contractor from  the responsibility stated in paragraph 1.1 above.

1.3   The equipments and systems covered in this specification shall be the design product of the manufacturer and shall be installed by the manufacturer’s approved authorized representatives .

1.4   Contractors price for panoramic lift shall include customs duties, sales tax and Jordan institute for standards and metrology ( JISM ) fees .

2.    DESCRIPTION & SCOPE OF WORK

2.1    The contractor shall provide all materials for complete electrical elevators, of 8 Passengers – 630 kg load , 5 stop,1m/s.

with all accessories and what ever necessary to complete work in perfect condition.

2.2   This contract shall cover the manufacture, testing at works,  full packing for  export, dispatch CIF, off loading, delivery to site, storing on site, complete erection, testing on site, commissioning to the entire satisfaction of the owner / engineer, maintenance and guarantee during the maintenance period (24 months from commissioning) following completion of the plant referred to in paragraph 2.1 above, complete with all auxiliary equipment and apparatus necessary for the safe, efficient and reliable operation .

2.3   The contractor shall submit 3 quotations for elevators from three different reputable manufacturers. The quotations shall be in full compliance with these specifications and contract terms. The owner / engineer shall reserve the right to  judge  and select on grounds of quality and price .

2.4   The contractor shall make good to the satisfaction of the owner / engineer any finish, surface, paving, decoration or the like, damaged or disturbed during the course of the  lift installation works.

2.5   This contract shall include, without any limitations to the foregoing, the manufacture, supply and installation of all steel supporting structures, frames and fitting, power and control equipment for the purpose of completing the systems specified.

2.6   Schedules give a summary of the required particulars. Spaces left blank in the schedules shall be completed by the tenderer.

3.   CODES, RULES & PERMITS:

3.1   All components and equipment shall be the most modern type and design for the service indicated shall be as nearly noiseless in operation as possible (Anti–noissance operation).

3.2  The work shall conform to the following codes:

European safety codes, British standard specifications, American standard specifications or approved equivalent .

Copies in English language of the complete safety regulations adopted shall be submitted with the tender documents.

4.   DRAWINGS

The contractor shall furnish drawings necessary to show the general arrangement of all equipment .

these drawings must be approved by the owner / engineer before work is begun. the drawing shall show the materials, details of construction and attachments to adjacent work of all trades for all work  required under this specification, complete wiring diagrams and conduit location and all other  pertinent data.

5.   WIRING DIAGRAMS

Complete wiring diagrams and single line diagrams showing the electrical connections, functions and sequence of operation of all apparatus connected with the work, shall be furnished to the employer in triplicate before first binding.

6.   MAINTENANCE

6.1   After the issue of the completion certificate, maintenance service for the equipment furnished under these specifications shall be provided for a period of 24 months. This service shall include regular weekly examinations of the installation during regular working hours by trained employees, and shall include all necessary adjustments, greasing, oiling, cleaning supplies and installation of a genuine standard parts to keep the equipment in proper operation.

6.2   Emergency call- back service shall be furnished during regular

working hours .

7. 	TESTS

7.1 	The contractor shall make all tests required by governing codes and such other tests, as stated under these specifications. All tests shall be witnessed by the engineer or his representative .

7.2   Any damage to the equipment caused by the tests or damage to the building caused by the failure of any part of this equipment to operate properly, shall be made good by the contractor to the owner / engineer satisfaction without any  expenses to the owner.

7.3   The contractor shall furnish all labour, material, power supply and instruments necessary for the required tests.

8    CLEANING UP

8.1  All excess materials and other debris which is a result of the works and all equipment  used in the execution of the works shall be completely removed from the premises.

9 	MACHINE AND DRIVE

9.1 	MACHINE

Each machine shall be of the worm Gearless traction type with motor, brake, gearing and driving sheave mounted in proper alignment on a cast iron or structural steel bed plate. the machine shall give car speed for all elevators. The worm shall be forged steel and provided with a ball bearing thrust designed to take the end thrust of the worm in both directions. Thrust shall be removable without removing the machine or the brake pulley.

9.2 	Construction And Location Of Machine (roomless).

The machine shall be placed at the top of lift shaft, upon structural steel beams or channels, which shall be furnished in place. The necessary fillings and bearing plates shall be supplied by the contractor. Sound insulation shall be rubber pads of proper density that effectively isolate the machine from the machine beams and flooring.

9.3 	Brake

The brake shall be spring applied, electrically released. it shall be instantly and automatically applied in case of power failure, and capable of holding the car under maximum load and speed conditions .

It shall be of self cooling type.

The brake shall be provided with manual release system in order to allow manual winding of the unit in emergency cases.

This emergency release set must be of self- resetting type.

9.4 	Pulleys

The traction sheave shall be of fine grained cast iron and be finished to give constant traction and long rope/Polyurethane Belt  life .deflective sheaves shall be of the same construction.

All the sheaves shall have approved bearings and supplied from an approved manufacturer.

Bearings for high speed lifts shall be of ball type,, bearing for low speed lifts shall be of bronze.

9.5 	Motors

All  motors shall be A.C. type specially designed and construction for the severe load conditions encountered in lift service, they shall be of the self- ventilating kind motors, and  shall be of high starting torque and low starting current and  comply with the requirements of this specification ( 180 start per hour for Speed>1 and not less than 150 S/H for Speed of 1m/s ).

The driving machine motor shall have sufficient capacity to operate continuously at 100% of contract speed and 100% of contract  load and for a ten minute period at 125% of contract load and at 100% of contract speed in both directions without overheating. Each motor shall have an auxiliary fan operated by a thermostat for cooling .

The motor shall  be suitable to work in good condition at 45c    (tropicalized).

9.6 	Machine – Motor Assembly

The machine and motor, brake, and bearings shall be mounted as one unit assembly on a common bed plate to ensure proper alignment and support.

Each lift machine shall be adequately isolated from the main building structure by means of approved material to  prevent  transmission of  noise and vibration.

“A steel Joist of adequate strength shall be furnished and fixed by the contractor in each machine room to facilitate lifting of the machinery”.

9.7.	Drive system:

Variable voltage variable frequency Gearless with permanent magnet synchronous motor with two independent brake system.

10. 	CAR AND AUXILIARIES

10.1 	Guiding And Guide Rails

Guides shall be of T sections of highest quality steel, for counter weight and car, accurately machined and polished .

the rails shall be connected together by means of strong steel splices plates, in proper alignment ( tungued joints ) .

These rails shall be fixed to the walls by heavy brackets welded to metal inserts in the wall, or can be fixed on steel structure shaft.

Number of brackets shall be selected so that the vibration is minimized, and shall be strong enough to with stand the sudden application of the safety gear under worst conditions (130% of the lift capacity). The brackets spacing shall not exceed 2 m.

the shoes shall be of the sliding type and shall run on the three rail surfaces . the car shall be properly balanced .

10.2 	Counter Weight

The counter weight shall be designed for smooth and economical operation, it shall be equal the car weight + (40%- 50%) of the load, and shall be of cast iron plates encountered by a steel frame, and fixed to it by means of tie rods .

Renewable guide shoes shall be fitted at the top and the bottom of the counter weight.

10.3 	Ropes

Suspension ropes shall be of special steel or high grade traction steel/ Polyurethane Belt , manufactured according to B.S. 329, or approved equivalent standard, the ropes shall be with safety factor not less than 16 times the capacity of the car and shall be provided with independent adjustment device for each rope, the governor ropes shall be of steel.

test certificates of the ropes legalized by authorized establishments shall be submitted to the owner / engineer for approval prior to shipment .

10.4 	Safety System And Governer

The car shall be provided with a safety system in order to stop the car in case the speed exceeds 1.15 the contract speed, or in case of failure of ropes of fastening. This system shall be actuated by a speed governor mounted in the machine room or above steel structure shaft (frame).

The system shall be (GRADUAL) and capable of  holding the car securely under the maximum loading  and governer tripping speed conditions, the safety clamping device shall consist of heavy jaws knurled roller, a lever assembly and other accessories to force the jaws and rollers against rails.

The governor, in addition to the operation of the safety system., shall disconnect the power from the motor, and the restoration of this power shall not be possible until the safety system has been manually reset .

10.5 	Safety Accessories

-   Luminous and acoustic signal for overload device.

-  Emergency independent light in car .

-  Inter- communication interphone with information  desk on ground floor (Three way intercom station)

-  Safety shoe for car door ( two sides ).

-  Independent operation .

-  Parking switch .

-  Attendant operation. Emergency exit at the top of car.

10.6 	Buffers

The buffers shall be of an approved design, of the rubber type, and shall be installed under the car and the counter- weight to stop them smoothly in case of emergency .

buffer location for the car and counter weight shall be shown on the drawing which shall be submitted to the engineer .

10.7 	Compensation Ropes

The suspension ropes and cables shall be counter balanced by compensation ropes and pulley, passing under the car and counterweight they shall be provided with a system that switches off the power to the car, when any defect or failure happens to the ropes or the pulley.

10.8 	Car Top Inspection

Car top inspection shall be located on the top of the car. This station shall permit the car to be operated at low speed by inspection and maintenance men.

10.9 	Alarm System

- The contractor shall furnish and fix a complete alarm system for the lifts. The alarm system shall comprise “ alarm” push- buttons in the cars, a central alarm bell luminous annunciator shall be located as directed by the owner / engineer .

- Contractor shall terminate all alarm D.C. supply circuits in terminal blocks at convenient points in the lift Hoistway, at the ground floor information desk ( rechargeable ).

- Contractor shall provide the conduit work and wiring between the annunciator and the terminal blocks and between different terminal blocks, in accordance with approved contractor’s drawings and diagrams.

- The alarm system shall operate in the following manner: whenever an alarm push- button in any of the cars is depressed, the central alarm bell shall ring loudly and the luminous annunciator shall identify the lift issuing the alarm signal . the annunciator shall continue to indicate until it is reset manually.

-  All components of the alarm system shall be of an approved manufacture, design and capacity. The tenderer shall submit full technical particulars of each component .

10.10 	Car Construction

The car shall be built of robust steel members.

The platform shall be of steel frame covered by a steel sheet of not less than 3 mm thickness, finally covered with fire resistance tiling. A steel sheet of not less than 26 gauge ( not less than 1.8mm ) shall protect the underside of the car to protect it against fire. The car frame shall be sound isolated from the main frame by means of rubber pads. The safety gear shall be mounted on the bottom members of each frame.

The interior of the car shall be of  brushed stainless steel. Flooring shall be of approved granite. Car shall be supplied with stainless steel handrail on three sides.

The car wall panels shall be well fastened to avoid vibration and to ensure rigidity.

Ceiling shall be of flat type, of steel structure and glass strong enough to receive 2 workmen .

Ventilation shall consist of one speed ventilator and concealed vent openings.

Car lighting shall be suitably provided and approved.

Ventilator and lighting shall be automatically switched on when the car is called, and shall continue to operate while car is in operation, and shall stop in 15 seconds after the car has stopped. Half of lighting shall be switched on always and half to be automatically switched off.

Sockets shall be provided for inspection lamps, on the roof and below the car.

A control station shall be full height placed in the car, in a convenient place, as specified herein after, in addition to a capacity and instructions plates.

The car shall be designed to carry the 1.3 x Cabine capacity load in kg.

10.11 	 Registration Of Landing Calls And Car Calls

Landing stations shall be provided at each landing entrance and car control station in the car. The system shall enable passenger to register the required direction by momentary pressure on the appropriate button. Floor push buttons at each floor shall also register a car call by momentary pressure.

Digital position indicators with direction arrows to be installed in all floors and in car.

11  DOORS

Car and landing doors shall be of the central opening horizontal  sliding automatic, power operated type, fire resistant, and of silent operation by  means of two points suspension ball or rolling bearing.

The button grooves and tracks shall be automatically cleaned by operation of the door .

All doors shall be provided with interlocks that prevent the operation of the car if any door is not completely closed .

It shall be possible to open any of the doors from the inside in case of power failure.

Car doors and any landing door of a stop floor shall open simultaneously and automatically on the arrival to the required floor and shall remain open for a sufficient period to allow leaving and / or entering the car, and it shall be possible to vary and adjust this period .

Doors shall be of brushed mirror stainless steel finish.

12  ELECTRIC DOOR OPERATOR :

-  An electric motor operated door operator of an  approved type shall be  provided to open and close the doors.

-  The operating device shall consist of an electric motor driving unit, and shall accelerate, smoothly in both direction of travel .

-  The necessary levers and door arms shall be designed to properly relate the motion of the door operation and the doors  pivot and bearing points in the door arms shall be steel, and bronze bushed pins or ball or roller bearings suitable for pressure lubrication.

-  The operating mechanism must be arranged so that just sufficient power is transmitted to the doors to operate them fully in both directions, and they must not close with a force such as to cause injury to children. In case of obstruction during closing, the power operator shall be reversed to return the doors to the fully opened position .

- Details of the operator shall be given by the manufacturer through the  tenderer .

13   SAFE- RAY:

Shall be double beam photo- electric device or curtain of light (COL) mounted on car lift between the car and landing doors.

Interruption of either light beam shall cause the door to remain open or, if closing to reopen .

14   SPEED AND CAPACITY

Elevators of 630 kg capacity shall have, speed of 1 m/second . The speed indicated in for the up direction travel with full capacity in the cars. The speed in either direction under any load condition shall not vary more than 5%.

15  CONTROLLER:

Controller shall be electronic computerized type control starting and stopping, and to provide the mentioned speed, controller shall also automatically apply the brake if any of the safety devices operate or the power fails for any reason .

Variable voltage and variable frequency (VVVF) control of start speed regulation must be used.

-  The controller shall provide protection and automatically disconnect motors against the following :

1.  no- volt and sustained under voltage.

2.  Over- current in any component .

3.  Phase failure and reversal of the power supply .

4.  Overload .

5.  Earth leakage current for motors above 1 h.p.

6.  Automatic fire return system.

7.  Automatic connection to stand-by generator .

8.  Serious unbalance of  phase winding currents for motors above 10 h.p.

9.  Heat sink temperature.

10.  Current sensor fault.

11.  speed supervision.

12.  Breaking resistor on time max 1 sec.

-  The controller shall be arranged to cut off the power supply, apply the brake, and bring the car to rest in the event any of the above failures occur.

-  The controller system shall operate from a rectified supply, 100 volts, D.C. or other approved D.C. voltage. Full details of the rectifier used shall be enclosed with the tender .

-	The elevator shall have the capability to operate in case of :

-+ 10% voltage variation .

-+  5% frequency variation .

16  LIFTS OPERATION:

Operation of panoramic lifts shall be simplex selective control

In case of power failure the lift shall go down to the nearest floor and doors shall be opened .

17.   CONTROL ACCESSORIES

17.1   Car Control Station

-  Two car control stations shall be mounted on full height mirror stainless steel panels, located in a convenient place in the car subject to the approval of  the engineer and shall contain the following :

1.  “UP” and “ DOWN” arrows.

2.  “ alarm” push.

3.  Floor pushes for each floor served.

4.  “ Start” push.

5.  Emergency “ stop” push.

6.  Car cut- out switch .

7.  Fan & light switches .

8.  Priority switch .

-  Maintenance and test switches shall be fitted on the top of the car .

-  the top of the car control station shall project above the car bodywork and  shall be fitted with a lamp and switch for use of the maintenance personnel. In addition a 5 amp. 3 pin socket outlet and switch shall be provided in this extended portion of the station, car ceiling shall be provided with emergency door.

17.2 	Directional Indicators

-  Electric indicator with directional arrows shall be fitted in the car to indicate to passengers entering the car, the direction in which the car will leave.

-  Combined electric indicator with travel direction signals and car – arrival gong shall be provided above landing entrance on each floor.

17.3   Position Indicators

Contractor shall provide position indicators as follows:

-  Position indicator above entrance inside car.

-  Presence and position indicator above the landing entrance at all floors.

17.4  	Emergency Key

An emergency of three  key suitable for opening all landing doors shall be handed to the purchaser after the work is completed.

18   LOAD WEIGHING DEVICE:

The car shall be provided with a load weighing system under the platform, which shall enable the car to bypass landing calls, and to stop the car departure in case the load exceeds the allowable load.

19  ELECTRICAL EQUIPMENT :

19.1 	General

-  Work described under these specifications shall include the supply and installation of all electrical equipment including wiring, metal boxes, conduits, mechanical components, electrical controls, safety features, control junctions, control cubicles, contactors, switches, circuit breakers, relays, protective equipment and all electrical equipment  necessary for the operation of the lifts .

-  All electrical wiring, equipment and motors shall comply with the conditions herein specified .

-  All wires, and cables shall be insulated with polyvinyl chloride base insulated  flame retardant ,1000 volt grade suitable for use in dry and wet locations

-  Alternatively mineral insulated copper conductor (MICC) cables may be used. Other types of wires which in the opinion of the contractor are of equivalent quality can be used, after being approved by the engineer . manufacturers of wires and cables shall be subject to the approval of the owner / engineer before placing any order with these manufacturers .conductors shall be copper stranded with P.V.C. insulation or solid with MICC cable ,or otherwise as will be approved by the owner / engineer.

-  All electrical wiring and equipment shall comply with the specified codes or relevant regulations.

-  Power and control cables operating at different voltages, or energized from different sources or phases shall be run inside separate conduits.

-   Travelling cables shall be provided for telephone, signals, controls, lights and fans of lifts.

-  Separate travelling cable shall be provided for alarm bell emergency circuit of  lifts cars.

-  Travelling cables for the lifts shall originate at steel junction boxes in hoistways and end at steel junction boxes on cars, hung so that proper size loop may be obtained. They shall have a fire and moisture resistant outer covering and contain a steel supporting strand.

Travelling cables shall be suitably suspended to relieve strains in individual conductors .

All electrically operated equipment shall comply in all respects with B.S.S. or approved equivalent standards, including dimensional standards where these exist .

All electrically operated equipment shall be so designed that it will continue to function without damage, to itself or others, if the voltage and / or frequency vary within the following tolerances :

Voltage – plus or minus ten percent (10%).

Frequency- plus or minus six percent (6%)

- Complete control wiring and schematic diagrams shall be submitted to the owner / engineer for approval before proceeding with manufacture of the equipment .

19.2	 General Construction

-  All electrically operated equipment shall be of robust construction, and shall have all current carrying and live parts and components insulated with materials in – class “B” or class “C” to B.S.S or equivalent standards subject to the approval of the owner / engineer. Motors shall be insulated with class “B” insulation to the same standards.

-  All electrically operated equipment shall be suitable for continuous and prolonged operation under the local ambient conditions. Allowance shall be made for local rises in air temperatures due to the operation of the equipment itself, or to heat produced in or by adjacent equipment .

19.3 	Electric Motors

-  All motors supplied under this specification shall be of approved manufacture. They shall be built and tested in accordance with the provisions of B.S.S  or equivalent standards. They shall be designed to give high starting torque and low starting current and shall be capable of running continuously at the predominating ambient temperatures.

-  All motors one (1) H.P. and above shall operate on 3- phase, fractional horsepower motors may operate on single phase. All 3- phase motors shall have current limiting or starting equipment which prevent the starting current exceeding twice full load current

-  Single phase motors shall have starting currents not exceeding six (6) times full load current. They shall be of the capacitor run type giving high power factor  and high efficiency, power shall be 0.95 or better at all speeds.

-  All motors shall be suitable for giving their full rated output, continuously with the voltage and / or frequency variation specified above , and shall be capable of restarting against full load in the event of the failure of supply.

-  The motors shall operate at different loads without undue noise or vibration.

-  Joints shall be made by electrical brazing or by other approved means.

-  All motors shall be provided with approved terminal boxes suitable to terminate the size and type of cable approved by the engineer. The terminal boxes shall be of ample sizes to enable connections to be made in a satisfactory manner .

19.4   Protection & Isolation Equipment

All overload trips of the thermal type shall be provided with automatic compensation for variations between the lowest and highest ambient temperatures available. All motors shall be provided with means of Isolation from the supply for purposes of adjustment and maintenance. Such means of isolation shall effectively interrupt the supply on all live contactors including neutral ( where it exist ) and shall be near to , and within sight of, both motor and starter. An additional isolator shall be used where motor and starter are out of sight of each other .

all motors, control gear, and ancillary equipment shall be protected by ( H.R.C) fuses in addition to any thermal, magnetic or other Overcurrent protection devices .

Where starter operating circuits and ancillary apparatus (e.g. push button) are energized by an auxiliary supply other than the main power circuit to the motor, the starters shall incorporate auxiliary contacts to effectively isolate all poles or phases of such auxiliary supplies. A clear schematic diagram of the circuits and components contained in the case shall be firmly fixed within the lid or cover of each starter, controller or cubicle.

All starters shall have at least two spare normally open auxiliary contacts over and above the auxiliary contacts needed for interlocks .

All components shall be provided with suitable cast or sheet metal cases into which screwed conduit can be connected, and shall be provided with substantial mounting brackets .

19.5   Earthing

All motors and control gear shall have their frames, carcases and all metal parts not normally carrying currents, effectively and continually connected to the general mass of the earth . each motor starter, regulator and other components shall be separately connected to the ring main earth conductor which shall be directly connected to the earth electrodes .

-  The main earth conductor shall have a cross section not less than half what is required to carry the current to the largest motor or other components which it protects.

20.  TERMINAL STOPPING DEVICES :

The lifts shall be equipped with automatic devices which shall stop the car at the terminal landing independent of the normal stopping devices. Final limit switches shall be provided to cut off the power supply and stop the car if it should overrun the normal stopping zones of the top or bottom landings.

21.  AUTOMATIC SELF- LEVELLING :

Automatic levelling shall be provided for all lifts. The maximum allowed levelling tolerance is ±5 mm. This accuracy shall be maintained regardless of speed change of load or rope stretch .

22.  PAINTING :

All exposed equipment metal work furnished under these specifications except as otherwise specified, shall be properly painted after installation .

23   TESTS ON SITE:

The following tests shall be carried out on each lift after completion of erection and prior to taking over :

-  Insulation tests on all wires and cables and resistance test of conduit system forming part of this contract .

-  Operating tests on power and control components.

-  Operation tests on safety gear with car fully loaded , without showing any sings of deformation .

-  Temperature rise tests on motor and controller, the temperature rise shall comply with accepted standards.

-  Load tests : in this test the car shall be loaded with weights equal to 150% the combined weight of  the car and its rated load. After 30 minutes the lifts shall not show any signs of permanent set .

-  Speed test : this test shall prove that in either direction the lift travels at rated speed with a maximum variation of plus or minus five percent  (5%) .

-  Levelling test to prove the lift complies with the requirements of the specification .

-  Any other tests requested by the owner / engineer to prove compliance of the lift with the specifications .

-  Testing and inspection shall be made approved and accepted by Jordan Institute for standards and Metrology .

24.  SUMMARY OF LIFT PARTICULARS:

Description	ONE Electrical lifts

Number of lifts 	1

Capacity (kg.)	1 No  of 630 kg

No. of passengers   8    passengers

No. of stops	5  stops

No. of openings   5 openings every left

Machine type 	A.C. gearless machine

Speed m./ sec.	1.0m /sec

Dimensions of shaftAs dwgs or according to manufacturers requirements.

Depth of pit (m) As dwgs or as required.

Access to pit	Yes

Height of floors in (m)As dwgs .

Material & thickness of Shaft walls	As dwgs with full co-ordination and requirement of lift supplier.

Power supply 	3ph. 400/230 V, 50 Hz

Connecting power (hp)	By supplier

Emergency lighting 	In cabin

Materials of counter – weight 	Cast iron blocks

Guide rails 	Sliding

Buffers	     rubber

Ventilating grills & fans in ceiling 	Yes  (Silent)

Interphone in cabin 	Yes (as per boq way intercom)

Car Door	Automatic two panel central opening s/s doors (mirror)

Landing doors	Automatic two panel central opening s/s doors (mirror)

Car walls	brushed stainless.

Car size	approved supplier size

25..  INFORMATION TO BE SUBMITTED WITH TENDER:

-  Outline arrangement drawings for each lift. Showing:

1.  General arrangement .

2.  Principal dimensions.

3. Details of building work required .

-  General arrangement drawing, of machinery showing principal parts and materials of construction.

-  General arrangement drawings of lift car showing principal parts and materials of construction, including method of attachment of ropes.

-   Schedule of principal parts other than mentioned above giving brief details of materials of construction of each and the standard to which it is manufactured .

-  Details of weights and their distribution necessary for design of the building structure ,

-  Standards and codes generally used in the manufacture of the lifts .

-  Car speed ( normal and levelling)., m/sec.

-  Approximate weight of car, kg.

-  Make and type of reduction gear .

-  Reduction ratio of winding machine.

-  Diameter of driving sheave.

-  Driving motor:

1.  Make & type.

2.  Rating , H.P.

3.  Type of bearing and method of lubrication .

4.  Type of rotor winding .

-  Method of levelling .

-  power consumed by control & other gear, watts.

-  Voltage of control circuits (v).

-  Type and full description of safety gear.

-  Method of  releasing brake in emergency .

-  Method of guide lubrication .

-  Particulars of guide rails.

-  Hoistway ropes:

1.  Number used .

2.  Diameter of each.

3.  Grade of steel tensile . strength , kg/ cm2 .

4.  Construction.

5.  Breaking strain, kg.

-  Proposed construction and finish of car and doors.

-  Proposed method of silent operation .

-  Details of door operation.

* Three types of well known and reputable elevators shall be submitted for approval (full package)  .

System Components Requirements

- Uninterruptible Power Supply (UPS)

- Contract calls for supply, install, connect, commission and maintain (U.P.S.)rating as per (dwgr & boq) Of the following characteristics:

- Fully automatic electronic circuitry, on line system suitable for computer use.

- Input Voltage Three phase 400V ± 10% Three phase, frequency 50 Hz ± 5%.

- Output Voltage Three phase 400V ± 1%, frequency 50 Hz ± 0.1%.

- Unit power factor (P.F=1).

- It can work 125% - 150% over load for minimum 10 seconds.

- It contains mimic panel with indicating lamps to show status of the  equipment. (Full status Indicators).

- Sealed lead – acid Batteries.

- Battery stand by period at full load for 15 minutes.

- Solid state equipment not servomechanism.

- Any changes in the voltage such as sags, Surges, Spikes transients and various noise should be eliminated.

- Fast response time (A 10% supply variation will be corrected within less than 0.3 sec.).

- Over load protection.

- High and low voltage shut off and Auto-reset.

- Short circuit protection – Auto shut – off and Auto Recovery.

- Low & High Voltage – Cut off + Auto Recovery.

- Wave form sin wave.

- Temp. Range 0 – 40 o C.

- Maintenance for Two years after commissioning including spare parts.

- Low noise level equipment [≤ 65 dB (A)] at 1 mt

- Original Catalogues in English Language to be supplied with the offer, two sets.

- Weight & Dimensions to be mentioned.

- Manufacturing origin and country to be mentioned.

- Supply and install a shutdown software (Under UNIX).

- Automatic / Manual Bypass is included.

- Maintenance Bypass with all accessories needed is included.

- Three types shall be submitted for approval.

- Bathe contractor shall remove the whole of the system and re-install a new similar one if an unsolvable problem occurred in the system.

- Lightning Protection System

GENERAL

The contractor shall supply and install the lightening protection system with MESH Principal and as herein specified. The system shall include air terminal, main and secondary conductors, grounding and all necessary parts to install a complete lightning system.

The system shall conform to the requirements of BS standard

AIR TERMINAL

Air terminal shall be (as per DWG) -long, 98% conductivity copper and pointed rod taper, mounted as shown on the Drawings, and shall extend fixed to the parapet with approved clamps and support.

MAIN & SECONDARY CONDUTORS

Conductors shall be of (as per dwg) mm2 bare standard copper conductors and copper tape 25x3 mm. Strand cross-section shall not be less than 2.5 mm2. Conductors shall be run down to pits with minimum of bends. Bends shall be of large radius (minimum 20cm). Bends less than 20cm radius shall be supported at two points not more than 7.5cm on each side from the center line of the bend. Conductor shall run down as far as possible from any structural or other metal bodies. They shall be concealed architecturally as much as practicable so as not to affect the facades of the building

SPLICERS AND CONNECTORS

Splicers and connectors shall be cast metals

GROUNDING TERMINALS

Each down conductor shall terminate in at accessible grounding pit, Clamps connecting down conductors to ground rod for a distance of 4 measured parallel to the axis of the ground rod with the cable itself for a distance of at least 4cm. Clamps shall be secured with at least two bolts or cap screws.

The resistance of the individual pits shall not exceed 50 ohms. The diameters of ground rod shall not be less than 1.5cm.

FASTENERS

Fastener shall be spaced not more than 1 m apart on all conductors. Nails, screws, or bolts employed to secure the Fasteners shall be of the same material as the Fasteners

Galvanized or plated steel nails or bolts are not acceptable mason anchors shall have a diameter of not less than 0.6 cm and shall be set with care holes to receive the shank of the fastener or fitting shall be of correct size made with proper tools and preferably made in the stones rather than in the mortar joints when set the fit shall be tight against moisture and capable of withstanding a pull test of 40 kg.

BONDING OF METALLIC BODIES

All metal parts of the building or requirement exposed to lightning strikes or within 60 cm of the lightning protection Fasteners shall be bounded to the grid by approved type of bolted connector .TV. antenna shall be bonded to the loop by a full-size copper cable a lightning arrester shall be installed on the lead in wire and bonded to the lighting protection system:

all connection of this nature shall be made with the use of splicers and fitting of an acceptable type.

All parts of the lightning protection system shall be manufactured in well known reputable manufacturers. And shall comply with BS standards, IEEE standards, or any other international standard.

The contractor shall submit one complete copy of system manuals and documentation.

The contractor shall guarantee the provided lightning system for two years. During guarantee period, the contractor shall be responsible for maintaining the system, replacing defected or damaged parts on his own account with no extra charges on the owner; also, the contractor shall remove the whole of the system and reinstall a new similar one if an unsolvable problem occurred in the system.

All calculations and shop drawings for the system shall be submitted by system agent through contractor for approval. All metallic parts on roof shall be connected to lightning system and drawings shall be submitted showing all details of connection and performance

- IP Based Video Surveillance System (CCTV) Specification

- 8.1	PART 1 – GENERAL

- Work Included

- Supply, install, test and commission complete IP Based Video Surveillance System (CCTV)

- 8.2	Reference standard

- i.	NEMA

- ii.	UL and CUL certified

- iii.	VDE & VDS

- iv.	BS-EN

- 8.3	Submittals

- a.	Submit product Data for approval including complete technical data and Manufacturer's catalogues for all equipment and materials.

- b.	Submit Manufacturer’s installation instructions.

- c.	Submit product Samples - one of each type.

- d.	Shop drawings and Construction drawings, submit drawings for approvalIncluding but not limited to the following:

- Details system schematic diagram

- Exact routing and layout of all cabling ways

- Typical installation details of cabinets, boxes and other equipment.

- 8.4	System Functionality

- The Video System shall provide for the following capabilities:

- a.	Viewing and Management

- The system shall not require proprietary or specialized viewing devices.

- The system shall provide for the management and viewing of all Cameras through the single IP address of a Video Relay Server.

- Users must have the capability for viewing and control of cameras by any of the following:

- 1.	A PC based browser

- 2.	A PC based client program including View Station software.

- 3.	The Management Server software or other software programs running with the Management Server.

- 4.	Third party software communicating with the Management Server.

- b.	Local and Remote Viewing and Management

- The system shall provide for viewing and control of cameras and setting of all system parameters using a browser over the network from a LAN or WAN connected PC, or through the Internet.

- The system shall allow the Management Server to be physically located anywhere so long as it is IP addressable through the LAN, WAN, or via the Internet.

- c.	Touring

- The system shall provide the ability to program “tours” for each Camera, directing it to move to a series of preset positions at designated speed, time sequence, and duration, and being able to take time stamped “snapshots” or storing video clips automatically at each preset view position.

- d.	Snapshots

- The system shall provide ability to capture, name, store and retrieve time stamped snapshots, and to copy, print, or e-mail them.

- e.	Password Protection

- The system shall provide for a minimum of four levels of passwords to restrict control of various functions to authorized individuals.

- f.	System Console

- System console functions shall be provided by View Station client software. From the View Station an operator shall be able to view live and stored video, control and view cameras, scan through system cameras, manage and view alarms and other aspects of the overall system. Layouts of multifunction and multi-up displays shall be fully user- definable and able to be displayed on multiple monitors. The system shall be able to initiate other system hardware and software activity as a result of scheduled events or alarm responses. The View Station client shall also provide the user the ability to:

- •	Group cameras by location, department, and other user-defined criteria.

- •	Schedule sequential camera and other system component activities.

- •	Create multiple custom operator console views.

- •	Sequentially view camera feeds through View Station live video windows.

- •	Configure automated alarm responses; view alarm conditions.

- g.	Alarm Management

- The system shall have the ability to accept a variety of alarm message types including MODBUS, telnet, FTP, SMTP, and TCP. Alarm messages must be parsed and managed by the Video Management software. Users must have the ability to define alarm responses on a per alarm basis, which may include audio and visual cues, video storage, camera movement, and operating system and 3rd party software commands.

- 8.5	SYSTEM COMPONENTS

- •	INDOOR CAMERA

- 	GENERAL REQUIREMENTS

- 	General:-

- The camera shall conform to the following requirements:

- 1.	The camera shall be designed to provide 1080p quality images via H.264 or M- JPEG compression up to 30 fps without compromising other features or performance.

- 2.	The camera must fully integrate to manufacturer’s NVR and VMS solutions, as well as offer integration to other 3rd party network recording solutions.

- 3.	The camera shall be part of the manufacturer’s own family of IP cameras and designed for 24 hour/7 day/365 day application use.

- 4.	The camera shall be delivered with a software CD (including installation guide, user manual, and manufacturer’s video management software), screwdriver and screws, and mounting template.

- 	Certifications and Regulatory:-

- The camera shall comply with the following:

- 1.	CE – EMC Directive 2004/108/EC, Standards EN55022, EN55024

- 2.	Low Voltage Directive 2006/95/EC

- 3.	FCC Part 15 Subpart B, ICES-003

- 4.	UL 60950-1

- 5.	RoHS Directive (2002/95/EC)

- 6.	C-tick

- 	PRODUCT REQUIREMENTS

- 	INDOOR DOME CAMERA:-

- 1.	The camera shall utilize a 1/3.0” format, CMOS Progressive Scan Imager.

- 2.	The camera shall provide a wide Dynamic Range of up to no less than 100dB.

- 3.	The camera shall have an integrated DC auto iris, aspherical 3-10mm remote zoom/focus glass lens.

- 4.	The lens shall incorporate a motorized zoom/focus lens with a focus assist feature

- 5.	The lens angle of view shall be at least 37.1 degrees to 115.2 degrees (horizontal).

- 6.	The camera shall have True Day Night functionality incorporating an integrated IR cut filter that switches depending upon the light level.

- 7.	The lens shall be an IR Corrected.

- 8.	The camera shall provide color images in light sensitivity ≤ 0.2 lux.

- 9.	Via a removable IR cut filter, the TDN camera shall provide black and white images in light sensitivity ≤ 0.08 lux

- 10.	The camera shall provide a shutter time of 1/10000 s to 1/25 s.

- 11.	The camera angle adjustment shall be at least 360 degrees for pan, 156 degrees for tilt, and 360 degrees for rotation.

- 12.	The camera shall accommodate digital pan, tilt and zoom via the camera web page and Manufacturer’s video management software.

- 13.	The camera shall incorporate a remote zoom feature whereby the focal length settings can be adjusted remotely.

- 14.	The camera shall include a focus assist feature that provides the ability to focus automatically during configuration.

- 	Video:

- 1.	The camera shall encode H.264 and M-JPEG video compression streams.

- 2.	The camera shall have options to provide progressive scan video in the following resolution formats:

- •	CIF (352 x 288 pixels)

- •	D1 (720 x 576 pixels)

- •	1080p (1920 x 1080)

- 3.	The preceding image detail shall be provided at capture rates of up to 30 Frames per Second (1920 x 1080). Other possible settings shall be 25, 15, 12,10, 8, 5, 4, or 2FPS.

- 4.	The camera shall be capable of accommodating at least two simultaneous streams of H.264 and M-JPEG compression streams, with any combination of compression, resolution and frame rates, in real time, at high video levels and low bit rates. As a minimum, the camera shall support full resolution on the first stream and D1 on the second. The possible stream options shall be as follows:

- •	Single or dual H.264 stream

- •	Single M-JPEG stream

- •	Simultaneous H.264 and M-JPEG streams

- 5.	The camera shall have constant bit rate (CBR) and variable bit rate (VBR) quality settings for H.264

- 6.	The camera shall have variable bit rate (VBR) quality settings for M JPEG.

- 7.	The camera shall provide options to remotely program any of the following features via an integrated web browser interface:

- •	Wide Dynamic Range

- •	Shutter time

- •	Iris aperture

- •	Iris gain

- •	Brightness

- •	Contrast

- •	Saturation

- •	Hue

- •	Sharpness

- •	White Balance Mode

- •	Auto day/night

- •	Mirror mode

- •	Frame Rate Base

- 	AUDIO:

- 1.	The camera shall have a line level audio input and output capable of providing full duplex, two-way stereo audio streaming.

- 2.	The camera shall provide the ability to encode audio data synchronized with video data. The audio compression protocol used shall be G.711 PCM and G.726 ADPCM compression.

- 3.	Where audio recording is to accompany video capture, the video and audio shall be synchronized to within ≤ one second for both live viewing and playback.

- 4.	Audio Frequency shall be configurable between 8 to 48 KHz.

- 	NETWORK:

- The camera shall have robust IP networking features, in line with IT management team expectations. These features shall include the following:

- 1.	The camera shall have programmable username and password protection, with LDAP authentication, for enhanced security

- 2.	The camera shall offer communication protection using HTTPS encryption for camera configuration and password entry.

- 3.	The camera shall operate using either DHCP or static IP addressing. If using DHCP addressing, client software must be able to connect to the camera using its new address without any action on the part of the user.

- 4.	The camera shall offer bandwidth limiting such that video data traffic on the network will not exceed a preset maximum when distributing live or recorded video.

- 5.	The camera shall support the following protocols:

- •	ONVIF

- •	RTP

- •	RTSP

- •	RTCP

- •	HTTP

- •	HTTPS

- •	IPv4

- •	TCP

- •	UDP

- •	DHCP

- •	ARP

- •	LDAP

- •	802.1X

- 	System Integration:-

- 1.	The camera shall be able to detect motion and trigger alarms based upon programmable Sensitivity and Threshold settings in at least four separate zones within the camera’s field of view.

- 2.	The camera shall offer an integrated industry-standard microSDHC memory card slot for local back-up of video. microSDHC recording options shall consist of continuous or motion based recording. When used with integrated VMS, the camera shall offer a Shadow Archiving feature such that the video recorded on the microSDHC card is accessible directly from compatible client software. In addition, recorded video can be recalled via the camera’s integrated web interface.

- 3.	The camera shall offer the ability to record directly to a NAS device independent of primary recording for applications requiring full redundancy. Video from the NAS shall be accessible via compatible client software. The camera, when used with integrated VMS solution, shall offer a Shadow

- Archiving feature such that the video recorded on the NAS device is accessible directly from compatible client software.

- 	FUNCTIONALITY:

- 1.	The camera shall have a three axis gimbal for positioning the camera and lens.

- 2.	The camera shall support a Power over Ethernet (PoE) Class 0 interface.

- 3.	The camera shall offer at least (as per boq) privacy zones when used with manufacturer’s video management software.

- 4.	The camera shall offer at least 3 privacy zones that are configurable within the camera

- 5.	The camera’s motorized zoom feature shall be capable of being locked by an administrator so users can’t adjust focal length settings.

- 	VIDEO Analytics:-

- 1.	The camera shall include a Video Motion Detection video analytic feature

- 2.	The camera shall include an Active Video Tampering video analytic feature to automatically determine if the camera’s viewing angle has change or it’s field of view has been tampered with

- 3.	Any of the aforementioned video analytic functions shall be used to trigger any of the following functions when combined with compatible client or system software:

- a.	Trigger recording to VMS via themanufacturer’s VMS software

- b.	Trigger an alarm, for both live viewing and historical searches

- c.	On Video Motion Detection, trigger recording to NAS or internally to SD

- 	Remote Access:-

- 1.	The camera parameters shall be programmed directly on the device via an integrated HTML web page. Settings such as video capture rates, compression formats, network streaming rates and more shall be controlled in this manner. The web page shall have a video window to display results of menu changes after they have been applied.

- 2.	The cameras shall have the ability to stream video in real time, with no appreciable delay or quality reduction other than limitations in the underlying network.

- 3.	The camera shall offer a virtual (digital) zoom capability of up to 50%

- 4.	magnification via the manufacturer’s video management software.

- 5.	Alarms shall be triggered by the detection of motion within at least four user- definable zones within the camera’s field of view.

- 	MECHANICAL:-

- 1.	The camera housing shall be light-weight plastic for internal installation, vandal resistant, with a polycarbonate transparent bubble.

- 2.	The camera housing shall incorporate an inner camera module with encapsulated electronics

- 3.	The overall dimensions shall be no greater than 9.85 cm H x 13.5 cm diameter(3.88” H x 5.31” diameter).

- 4.	The camera shall weigh no more than 490g (1.08 lb).

- 5.	The camera housing shall accommodate direct mounting in a surface mount configuration with a single housing, without the need for any additional mounting accessories.

- 6.	The camera shall be offered with optional accessories for flush mount, to mount on walls, poles and from ceilings, or side access for mounting to concrete or other hard surfaces

- 7.	The mounting accessories shall be 1.5” NPT for mounting the camera to industry standard 1.5” NPT mounts.

- 	ELECTRICAL:

- 1.	The camera shall be powered from a PoE IEEE 802.3af Class 0 device.

- 2.	The camera shall have a power consumption ≤ 3W

- 	ENVIRONMENTAL:

- 1.	The camera housing shall be light-weight plastic and intended for indoor use

- 2.	The camera shall have an operating temperature of at least -10 to 50C (-14 to 122F).

- 3.	The camera shall have a Relative Humidity of 0-90 % non-condensing.

- 	SOFTWARE Development Kit (SDK):

- The camera shall also offer a comprehensive Software Development Kit (SDK) that shall provide for the integration to third party security and application solutions. This SDK shall have the following characteristics:

- 1.	The SDK shall provide a comprehensive set of industry-standard ActiveX controls for broad third-party application development and system integration.

- 2.	Interfaces to a number of third-party systems shall have already been developed and maintained (using this SDK or otherwise), and these integrations shall be available to new customers as appropriate.

- 3.	For new application integration, the SDK shall enable application access to view cameras.

- •	OUTDOOR BULLET CAMERA

- 	GENERAL REQUIREMENTS

- 	GENERAL:

- The camera shall conform to the following requirements:

- 1.	The camera shall be designed to provide 3MP quality images via H.264 or M- JPEG compression up to 15 fps without compromising other features or performance.

- 2.	The camera must fully integrate to manufacturer’s NVR and VMS solutions, as well as offer integration to other 3rd party network recording solutions.

- 3.	The camera shall be part of the manufacturer’s own family of IP cameras and designed for 24 hour/7 day/365 day application use.

- 4.	The camera shall be delivered with a software CD (including installation guide, user manual, and manufacturer’s video management software), L-wrench, and C-mount adaptor.

- 5.	The camera shall offer wide angle and varifocal lens options directly from the manufacturer.

- 6.	The camera shall be offered with an optional environmental housing directly from the manufacturer.

- 	CERTIFICATIONS and Regulatory:

- The camera shall comply with the following:

- 1.	CE – Standards EN55022, EN55024

- 2.	FCC Part 15 Subpart B, ICES-003

- 3.	RoHS Directive (2002/95/EC)

- 4.	C-tick

- 	PRODUCT REQUIREMENTS:-

- 	OUTDOOR BULLET CAMERA

- 1.	The camera shall utilize a 1/2.8” format, 3 Megapixel, CMOS Progressive Scan Imager.

- 2.	 The camera shall provide a Wide Dynamic Range of up to no less than 100dB.

- 3.	The camera shall have True Day/Night functionality incorporating an integrated IR cut filters that moves depending upon the light level

- 4.	The camera shall provide color images in light sensitivity ≤ 0.2 lux.

- 5.	Via a removable IR cut filter, the TDN camera shall provide black and white images in light sensitivity ≤ 0.02 lux.

- 6.	The camera shall provide a shutter time of 1 s to 1/10000 s.

- 7.	The camera shall provide manual and automatic white balance.

- 	VIDEO:-

- 1.	The camera shall encode H.264 and M-JPEG video compression streams.

- 2.	The camera shall have options to provide progressive scan video in the following resolution formats:

- •	CIF (352 x 288 pixels) secondary stream

- •	D1 (720 x 576 pixels) primary and secondary streams

- •	720p (1280 x 720 pixels) primary stream

- •	Full HD (1920 x 1080 pixels) primary stream; H.264 only

- •	3MP (2048 x 1536) primary stream; H.264 only

- 3.	The preceding image detail shall be provided at capture rates of up to 30 Frames per Second (1920 x 1080). Other possible settings shall be 15, 10, or 5FS.

- 4.	The camera shall be capable of accommodating at least two simultaneous streams of H.264 and M-JPEG compression streams, with various combinations of compression, resolution and frame rates, in real time, at high video levels and low bit rates. As a minimum, the camera shall support full D1 on both streams. The possible stream options shall be as follows:

- •	Single or dual H.264 stream

- •	Single M-JPEG stream

- •	Simultaneous H.264 and M-JPEG streams

- 5.	The camera shall have constant bit rate (CBR) or variable bit rate (VBR) quality settings for H.264.

- 6.	The camera shall have variable bit rate (VBR) quality settings for M-JPEG.

- 7.	The camera shall provide options to remotely program any of the following features via an integrated web browser interface:

- •	WDR

- •	Anti-flicker

- •	White balance mode

- •	Brightness

- •	Contrast

- •	Saturation

- •	Hue

- •	Sharpness

- •	Auto Day/Night

- •	Mirror mode

- •	Auto iris

- 	AUDIO:-

- 1.	The camera shall have a mono mic audio input and stereo line output capable of providing two-way mono audio streaming.

- 2.	The camera shall provide the ability to encode audio data synchronized with video data. The audio compression protocol used shall be G.711 PCM and G.726 ADPCM compression.

- 3.	Where audio recording is to accompany video capture, the video and audio shall be synchronized to within ≤ one second for both live viewing and playback.

- 4.	Audio Frequency shall be configurable between 8 to 48 KHz.

- 	NETWORK:

- The camera shall have robust IP networking features, in line with IT management team expectations. These features shall include the following:

- 1.	The camera shall have programmable username and password protection, with LDAP authentication, for enhanced security.

- 2.	The camera shall offer communication protection using HTTPS encryption for camera configuration and password entry.

- 3.	The camera shall operate using either DHCP or static IP addressing. If using DHCP addressing, client software must be able to connect to the camera using its new address without any action on the part of the user.

- 4.	The camera shall offer bandwidth limiting such that video data traffic on the network will not exceed a preset maximum when distributing live or recorded video.

- 5.	The camera shall support the following protocols:

- •	ONVIF

- •	RTP

- •	RTSP

- •	RTCP

- •	HTTP

- •	HTTPS

- •	IPv4

- •	TCP

- •	UDP

- •	DHCP

- •	ARP

- •	LDAP

- 	SYSTEM Integration:

- 1.	The camera shall be able to detect motion and trigger alarms based upon programmable Sensitivity and Threshold settings in at least four separate zones within the camera’s field of view.

- 2.	The camera shall offer an integrated industry-standard microSDHC memory card slot for local back-up of video and audio. MicroSDHC recording options shall consist of continuous or motion based recording. When used with integrated VMS, the camera shall offer a Shadow Archiving feature such that the video recorded on the microSDHC card is accessible directly from compatible client software. In addition, recorded video and audio can be recalled via the camera’s integrated web interface

- 3.	The camera shall offer the ability to record directly to a NAS device independent of primary recording for applications requiring full redundancy. Video from the NAS shall be accessible via compatible client software. The camera, when used with integrated VMS solution, shall offer a Shadow Archiving feature such that the video recorded on the NAS device is accessible directly from compatible client software.

- 4.	The camera shall support Internet Explorer (7.0 or higher).

- 	FUNCTIONALITY:

- 1.	The camera shall support a Power over Ethernet (PoE) Class 2 interface.

- 2.	The camera shall support 12 VDC with a power consumption of ≤ 4W.

- 3.	The camera shall provide an integrate alarm input and relay output (open collector).

- 4.	The camera shall support active video tampering to notify users (via the head- end system) if the camera’s field of view has been obstructed or moved.

- 5.	The camera shall offer at least (as per boq) privacy zones when used with manufacturer’s video management software.

- 	REMOTE Access:

- 1.	The camera parameters shall be programmed directly on the device via an integrated HTML web page. Settings such as video capture rates, compression formats, network streaming rates and more shall be controlled in this manner. The web page shall have a video window to display results of menu changes after they have been applied.

- 2.	The cameras shall have the ability to stream video in real time, with no appreciable delay or quality reduction other than limitations in the underlying network.

- 3.	The camera shall offer a virtual (digital) zoom capability of at least 50% magnification via the manufacturer’s video management software.

- 4.	The camera shall support the integration of video and bi-directional audio streams, enabling personnel at the central facility to communicate in real-time with persons at any remote site equipped for this type of interaction.

- 5.	Alarms shall be triggered by the detection of motion within at least four user- definable zones within the camera’s field of view.

- 	MECHANICAL:-

- 1.	The camera housing shall be constructed of powder-coated aluminum.

- 2.	The camera shall incorporate a DC drive auto iris.

- 3.	The camera shall incorporate an internal microSD/SDHC memory card slot.

- 4.	The overall dimensions shall be no greater than 7.85 cm W x 13.13 cm L x 4.83 cm H (3.09” W x 5.16” L x 1.9” H).

- 5.	The camera shall weigh no more than 0.3 kg (0.66 lbs).

- 6.	The camera housing shall accommodate mounting options for the following applications:

- •	Indoor wall mount

- •	Outdoor wall mount (with environmental housing)

- •	Outdoor ceiling mount (with environmental housing)

- 	ELECTRICAL:

- 1.	The camera shall be powered from a PoE IEEE 802.3af Class 2 device.

- 2.	The camera shall have the capability of being powered from 12 VDC.

- 3.	The camera shall have a power consumption of ≤4W.

- 	ENVIRONMENTAL:

- 1.	Without its optional environmental housing, the camera shall have an operating temperature of at least 0° to 50C (32° to 122F).

- 2.	When used with its optional environmental housing, the camera shall have an operating temperature of at least -40° to 50C (-40° to 122F).

- 3.	The camera shall have a Relative Humidity of 8-90 % non-condensing.

- 	SOFTWARE Development Kit (SDK):-

- 1.	The camera shall also offer a comprehensive Software Development Kit (SDK) that shall provide for the integration to third party security and application solutions. This SDK shall have the following characteristics:

- 2.	The SDK shall provide a comprehensive set of industry-standard ActiveX controls for broad third-party application development and system integration.

- 3.	Interfaces to a number of third-party systems shall have already been developed and maintained (using this SDK or otherwise), and these integrations shall be available to new customers as appropriate.

- 4.	For new application integration, the SDK shall enable application access to view cameras.

- 5.	The SDK shall enable the application access to audio streams in addition to video data.

- 	Novib Compliancy:

- The camera shall be ONVIF-compliant, allowing it to be used with a variety of third party systems. When used in conjunction with an ONVIF-compliant system, the camera shall support the following features:

- •	Discovery

- •	Stream Configuration

- •	Audio Streaming

- •	Video Streaming

- •	Privacy Masking (provided the third-party system supports this feature)

- •	Digital Zoom (provided the third-party system supports this feature)

- •	H.264

- •	M-JPEG

- •	CCTV NETWORKED DIGITAL VIDEO RECORDER AND TRANSMISSION SYSTEM

- 	GENERAL REQUIREMENTS

- 	GENERAL:

- NVR Unit Characteristics

- Combined with Visual Intelligence Software, the NVR unit shall have the following characteristics:

- 1.	The system shall be a networked device purpose built exclusively for the capture and processing of digital video and supporting audio, alarm, storage and other services. The system shall not be based on generic industry PC components and architectures.

- 2.	The NVR platform shall have an option use docking station architecture, marrying a removable 2U-high NVR chassis (containing all system and video processing and storage components) with a fixed housing capable of mounting in a standard 19” equipment rack and accepting power, camera, network and other wiring connections. The NVR platform shall also be available in a desktop style chassis when installation in a rack is not required.

- 3.	The NVR shall employ an embedded Linux operating system, housed in flash memory and capable of being upgraded remotely if needed, such that no system software shall be stored on hard-drive media, and the operating environment shall be more robust and immune to virus and illicit attack than other common operating systems. At the client desktop, however, all software applications shall support the latest Windows® operating environments.

- 4.	The NVR shall provide for choice when selecting a software interface for either an integrated browser based client or a tasked based suite of installable clients.

- 5.	Once a software interface has been selected, the NVR shall employ a common software interface regardless of the model selected. This will yield consistent user training materials, documentation and system interaction.

- 6.	The NVR shall provide a ‘hybrid’ architecture, capable of supporting traditional analog cameras in the quantities shown below as well as a number of IP cameras (see below) to increase the aggregate camera support, provide high- resolution video capture in critical customer areas, and allow migration to this new camera technology according to customer need.

- NVR Unit Configuration

- The NVR unit shall be available in the following configuration common across all models:

- 1.	4 audio inputs, 2 which can support bi-directional, half-duplex input/outputs

- 2.	8 alarm inputs and 4 switch outputs

- 3.	1 RS-232 ports, 1 RS-485 ports for integrating banking ATM/Teller transaction or retail POS transaction capture information and PTZ camera controllers, and 4 USB 2.0 data port for connecting keyboard, mouse, or external media for export purposes

- 4.	1 RJ-45 Gigabit Ethernet network connection for LAN-based system access and management

- 5.	1 RJ-45 Gigabit Ethernet network connection for connecting IP cameras and encoders on a network separate from the corporate LAN

- 6.	Up to 4 internal, high-capacity, SATA hard disk drives, supporting up to 3TB each, and mounted for easy servicing

- 7.	1 internal back-up battery for filtering out power fluctuations

- 8.	2U-high docking-station chassis for simple mounting and servicing in a standard 19” equipment rack or a 2U-high desk top chassis if rack mounting is not required.

- 9.	BNC video inputs as per boq (with software controlled loop-through capability) able to accept NTSC or PAL composite signals

- 10.	1 composite video output (NTSC or PAL) capable of displaying both analog and IP cameras in a programmable sequence.

- 11.	1 HDMI video output capable of displaying both analog and IP cameras in a high definition user interface for live display and archive searching.

- 12.	240 or 480 frame-per-second (FPS) aggregate video capture for the analog inputs (based on the model selected), supporting CIF and 4CIF video format [NOTE: Select only the unit necessary for the project]

- 13.	48 Mbps of bandwidth supporting up to (No. as per boq) IP cameras when (No. as per boq) analog inputs are enabled or 96 Mbps of bandwidth supporting 32 cameras (depending on model selected) allocated to IP camera support. IP cameras should be configured to provide an appropriate video stream for the capability of the model selected.

- a.	Configuration and Viewing Applications

- The Visual Intelligence configuration and viewing applications shall be compatible with the latest version of Windows®. Each application shall be installed from a CD using an automatic installation program. All applications shall have similar interfaces in order to reduce learning time, and shall operate consistently across all members of the NVR product family.

- The Command Enterprise configuration and viewing applications shall be compatible with the latest version of Windows® or MAC O/S. The integrated application shall be installed on the Command Enterprise server from a CD using an automatic installation program. Once installed on the Command Enterprise server, the application can be accessed by any operator on the network via a supported browser.

- Concept of Operation

- 1.	The NVR unit shall capture, digitize and compress video (using industry- standard H.264 video compression technology and multi-level encoding to further optimize transmitted and stored video) and, if desired, accompanying audio signals on all enabled inputs. Once compressed, the unit shall either distribute the compressed data to any number of authorized users requesting the data over either of the unit’s network ports from one of the supported application interfaces (Command Enterprise or Visual Intelligence).

- 2.	In parallel, the unit shall also store all compressed data to the available internal hard disk drive(s). These internal drives shall be expandable by the user, from a single drive configuration through to 4 high-capacity drives for extensive in- system storage.  This in-system storage shall be capable of being set up in an offset mirrored configuration where 1 drive can be mirrored with 3 drives.

- 3.	Internal system storage shall take advantage of Intelligent Video Archiving and Retention technology that uses the concept of retention rather than recording. A retention based system captures, by default, video from all connected cameras at the highest per-camera frame rates available on the unit (based on model selected), and providing always-on high quality recording on all cameras in keeping with the FBI/Scientific Working Group on Image Technology [SWGIT] recommendations. The user shall then be able to set up rules to determine when the retained video is to be removed from the recorder and which video is to be retained.

- 4.	After the all of the attached storage has been filled, video of potential interest (e.g., motion video, alarm video, retail or financial transaction video) is reviewed according to the set rules and if tagged, is moved into the Longer-Term Storage area. All other video is removed and the disk space freed up by this ‘thinning’ process shall be available for new video storage. Beyond long-term storage, a further Extended-Term Storage area shall be available to further thin and retain critical video for an extended period of time.

- 5.	At any time, selected video/audio data shall be available for export by users across the network to their PCs as well as through a USB-connected media storage device (e.g., USB memory stick or USB hard drive) at the NVR. This video shall be completely appropriate for use in evidentiary purposes, and shall include a security (authentication) seal for continuity purposes and an auto-run Evidence Reviewer’ utility for playback and assessment by third parties such as law enforcement officials.

- 6.	The unit shall simultaneously handle recording, retrieving, and live distribution of video and audio. The unit shall operate in a continuous record mode, even if only event driven recordings, scheduled recordings or motion detection recordings are to be retained for longer periods of time. The unit must be capable of independent operation with network access and control, centralized management in conjunction with a number of other NVR units, or operation under the control of a centralized, enterprise-level suite of multiple-system management software.

- b.	System Security

- 1.	The unit shall be able to mount on a desktop, wall, or particularly, inside a19” equipment rack with a secure docking station, and have a removable but secured top cover such that the unit cannot be easily powered down or have the disk drive(s) accessed inappropriately

- 2.	Each NVR shall be deployed almost exclusively ‘behind’ an existing network security firewall, benefiting from the default virus protection software and encryption options of that equipment to prevent hacker attacks. In addition, the NVR shall be capable of existing securely on an unprotected network, thereby providing superior security performance relative to most other video systems available.

- 3.	Each NVR shall use an embedded (in flash memory) Linux operating system, which is inherently more robust in architecture and less susceptible to virus and other “hacker” attacks than other operating systems. Each NVR shall minimize the number of access points for hackers to try and gain access to the unit or by which a virus may attack the unit. Communications with the NVR shall be very restricted, with most external ports being blocked and no way made available to open them. Communication between all entities in the system (client software, management server software, and NVRs) shall be encrypted using SSL encryption.

- 4.	The NVR unit shall not share any known or unknown vulnerabilities associated with popular PC or computer operating systems. It shall achieve a C2 level of security. All TCP and UDP ports not required for use will be blocked thus ensuring that points of network attack will be minimized.

- 5.	The NVR unit shall operate without the requirement for a keyboard, monitor or mouse - also known as ‘headless’ operation – instead being controlled across the network from authorized client PCs. As a result, no tampering shall be possible at the unit itself.

- 6.	All analog video shall be captured and transmitted to the NVR over coaxial cables, directly connected to the rear of the units. No interception of these video streams shall be possible without physically tapping into the specific cable inside the customer premises.

- 7.	 All IP-camera-based video shall be captured and transmitted to the NVR using the IP protocol. The NVR shall have the capability of connecting with the cameras either through a routed network or directly via the IP camera card.

- 8.	The NVR unit shall allow for the use of password authentication to prevent unauthorized access to the NVR. Two levels of authentication shall be supported (user and administrator) when the NVR is managed in a peer-to- peer fashion. When the NVR is being managed by server-based management software, the system shall support a large number of users and user groups, as well as a rich set of privileges. In this enterprise configuration, external user authentication using an existing enterprise application shall also be supported, providing the net effect for users of ‘single sign-on’ or single authentication through their traditional system access utility.

- 9.	The NVR shall ensure command and control data packets are encrypted for network transmission using SSL security technology NVR.

- 10.	The system shall provide the ability to limit operator access to NVR resources. Administrators shall be able to manage user rights to a fine granularity of control, down to the level of access to the individual resource (for example, a single camera, audio channel, or data port).

- 11.	The local or centralized system administrator shall be able to access all NVR units that are visible on the network, subject to each user’s privilege level. Each individual NVR unit shall keep a log of any user access to the unit. The log shall be retrievable remotely by an administrator, but no user will be able to remove entries from the log. The log shall be maintained automatically by removing entries that are six months old. It shall be an option to copy and save the report to a text-formatted file for import into a third party application. It shall be an option to print the report. These capabilities shall be scalable such that they will work seamlessly under the control of a centralized, enterprise-level suite of multiple-system management software.

- c.	System Management

- All NVR units shall be capable of being managed locally or centrally over a TCP/IP LAN or WAN network, using individual system or enterprise-level management utilities.  All systems shall be capable of being managed by a set of consistent user interface applications that operate consistently across all members of the NVR product family. The enterprise-level management application shall be capable of managing system programming, monitoring the health of the system in real-time, of upgrading the software on an NVR unit, synchronizing the time on an NVR unit, remotely managing an NVR unit, and more. Reports on systems use, problems, and alarms shall be capable of being printed. Reports shall also be capable of being copied or saved for importing into third party applications.

- d.	 Automated Configuration

- As NVR units are added to the network, the NVR management application shall automatically detect their presence on the network to support rapid configuration and administration.

- e.	Reliability

- 1.	The NVR shall use an embedded (in flash memory) Linux operating system, which is inherently more robust in architecture and reliability than other operating systems.

- 2.	No NVR operating software shall reside on the NVR hard-drives, eliminating hard-drive failure as a reliability issue and allowing the unit to operate without any hard-drives present (e.g., in a video streaming application, or when utilizing external storage).

- 3.	The NVR unit shall contain hardware and software watchdog circuitry that maximize fault-free operation. The central management application shall report all problems detected by any NVR units on the network. The NVR configuration software shall continuously supervise the health of both the unit and the network, including dial-up extensions. The management utility shall periodically connect to all dial-up connected NVR units in order to ascertain the health of both the unit and the line/modem on which the unit is connected.  An option to ‘connect on demand’ shall also be provided to support low-activity NVR deployments.

- 4.	The NVR shall use SMART disk technology to provide real-time monitoring of all internal hard-disks, including diagnostics and health reporting, to provide further system reliability.  The unit shall offer internal disk mirroring in a multi-drive configuration to further protect stored data.

- 5.The administrator shall control the level of problem reporting (thresholds) in order to ensure the reliability of the NVR and the equipment connected to the  NVR  unit,  but  also  to  manage  the  amount  of  communications consumed by this activity. The administrator shall be able to have notification of problems e-mailed to specific users.

- f.	Video Capture

- 1.	The video compression protocol used by the NVR unit shall be H.264, which uses an inter-frame mechanism to assist in achieving the optimum compression.

- 2.	The NVR shall have an aggregate capture rate of 480 fps (NTSC) or 400 fps (PAL) across its (No. as per boq) analog inputs, depending on the model selected. On all units, five (5) levels of compressed video quality shall be supported to balance desired video clarity against available hard drive storage.

- 3.	Video capture rates shall be allocated in a flexible manner per camera, with different frame rate settings on each camera. Frame rates can be set anywhere from 1 fps up to 15 or 30 fps per camera input, respecting the limit of the model selected.

- 4.	Per-camera video capture rates shall have the option of being increased (to the maximum available based on system capability) on alarm or event triggering (i.e., detection of motion, activation of a panic alarm button, etc.).

- 5.	The NVR shall be capable of capturing and distributing video at high frame rates while storing at a lower frame rate or vice versa. Display resolutions shall be: NTSC - CIF (352 x 240 pixels), and 4CIF (704 x 480 pixels); PAL –CIF (352 x 288), and 4CIF (704 x 576).

- g.	 Video Loss Detection

- The NVR unit shall constantly supervise all enabled video inputs for a synchronization signal and, if enabled, notify the administrator of signal loss. Video sync loss detection shall be filtered to ensure that brief interruptions are masked and problem cameras do not generate excess alarms.

- h.	Field of View Monitoring

- Using video analytic capabilities, the NVR unit shall also provide camera obstruction detection and scene change detection. Both applications will offer user-programmable learning parameters, and alert thresholds, and can be used together or independently.

- i.	 Video Output

- The NVR unit shall have looping video inputs plus a single video output which is capable of displaying video from selected camera inputs in a sequenced display application, with a programmable dwell sequence being available for each display. This sequence shall be interruptible in order to display specific video related to an event (i.e., alarm trigger) on the NVR unit, and shall return to the preset sequence once that event has completed.

- j.	 Audio Capture

- 1.	The NVR shall provide the ability to record 4 channels of audio data synchronized with video data. Audio recording shall be 2-way, half-duplex communication on 2 of the channels. The audio compression protocol used shall be ADPCM compression. Four levels of Audio compression (quality) shall be supported.

- 2.	Where audio recording is to accompany video capture, the video and audio shall be synchronized to within one second for both live viewing and playback.

- 3.	Audio shall be recorded separate and distinct from the video such that it can be associated after with any video stream after it has been recorder.

- k.	Storage

- 1.	Each NVR shall support 1 through to 4 internal hard disk drives to provide high-capacity video storage, with the drives having a capacity of at least 3TB each or larger. No system (NVR) software or operating system elements shall reside on these hard drives, thereby avoiding any reduction in video storage capacity and increasing system robustness

- 2.	The NVR unit shall contain no removable media for off-line storage. All storage shall be on-line for as long a period as possible based on the configuration that has been selected. Configurable parameters for altering storage duration shall include:

- •	Display size (CIF, 2CIF, 4CIF)

- •	Frame rate

- •	Video quality settings (most detailed, more detailed, medium, more compressed, most compressed)

- 3.	Internal system storage shall take advantage of Intelligent Video Archiving and Retention technology that uses the concept of retention rather than recording. A retention based system captures, by default, video from all connected cameras at the highest per-camera frame rates available on the unit. This provides an always-on high quality recording on all cameras in keeping with the FBI/Scientific Working Group on Image Technology [SWGIT] recommendations. The user shall then be able to set up rules to determine when the retained video is to be removed from the recorder and which video is to be retained.

- 4.	After all of the attached storage has been filled, video of potential interest (e.g., motion video, alarm video, retail or financial transaction video) is reviewed according to the set rules and if tagged, is moved into the, Longer-Term Storage area. All other video is removed and the disk space freed up by this ‘thinning’ process shall be available for new video storage. Beyond long-term storage, a further Extended-Term Storage area shall be available to further thin and retain critical video for an extended period of time

- 5.	All video shall be stored at the NVR unit and only be delivered over the network when either the recorded video is searched and retrieved or if live video is requested.

- l.	Recorded Information

- The information recorded on the NVR unit shall consist of the following data:

- 1.	Compressed video

- 2.	Compressed audio

- 3.	Time stamp consisting of date and time with millisecond resolution

- 4.	Associated event information

- 5.	Associated transaction information (for example, retail Point-of-Sale or ATM/Teller financial transactions)

- 6.	Audit information

- m.	Recorded Format

- Compressed video from all cameras shall be stored in such a way that it is independently retrievable. Compressed audio shall be stored in such a way that it is independently retrievable or can be associated with any video input. When a video recording with associated audio is retrieved, the audio shall be retrieved automatically (synchronized) along with the video. The operator shall be able to retrieve a video clip from the NVR unit at any file size up to a maximum of 2.0 GB.

- n.	Continuous Recording

- The NVR unit shall be capable of recording continuously on each video and its audio input. The capacity for recording shall not exceed 40 GB when recording continuously for 7 days on 4 cameras at 15 fps, with a “More Compressed” setting and moderate to low motion. Capacity for recording on IP cameras shall be dependent on the configuration settings of the IP camera.

- o.	On-Event Recording

- 1.	The NVR unit shall be capable of recording any video input (and associated audio if desired) in response to an external alarm. The recording period shall be of any duration from 30 seconds to seven days. There shall be no hard association of an external alarm to a camera or audio source. Any alarm can cause an action to record on any or all cameras and the audio input.

- 2.	Optionally, any given camera shall be programmable to record at up to the maximum capture rate (fps) available from the system in response to an alarm.

- 3.	Events that trigger long or extended-term retention shall include:

- •	Any external closed current loop device connected to the NVR unit(door sensor, motion sensor, etc.)

- •	Motion in the video image (in the image overall, or in individual and configurable ‘masked’ areas of the image, with configurable sensitivity settings)

- 4.	Extended retention on video motion detection shall be tunable using full screen sensitivity setting to simplify configuration or using a user definable grid for area of interest. In order to reduce the frequency of motion alarms, the detection of next occurrence of motion can be delayed until there is a period of inactivity in the image. Detection of video motion shall be capable of being enabled during specific periods of the day according to a pre- determined schedule.

- p.	Scheduled Recording

- The NVR unit shall be capable of executing any number of internal recording schedules defined by the administrator. Schedules shall be remotely configurable and control the following actions:

- 1.	Extended retention (any combination of cameras for any duration from 30 seconds to 7 days)

- 2.	Monitoring of physical alarms (during specified periods)

- 3.	Monitoring of motion alarms (during specified periods)

- 4.	Increase of the bandwidth throttle

- 5.	Assertion of a switch (for a specified period)

- 6.	Moving of a PTZ unit to a predefined position

- 7.	Displaying of a specific camera on the spot monitor

- q.	Time Synchronization

- The NVR unit shall allow for clock synchronization to occur manually or from a central location through a network time protocol (NTP) server or enterprise management server. The NVR unit shall also be capable of automatically adjusting the clock to Daylight Saving Time, and adjusting for deployment in varying time zones

- r.	Live Video/Audio Viewing

- The NVR viewing application shall be capable of displaying up to 36 video windows simultaneously in a 6 x 6 grid with video from cameras on the same NVR as well as video from different NVRs. Live video windows shall be able to co-exist on one monitor or across several, with playback windows on the same screen from within the same application. Each video/audio window shall have independent control and all windows shall be capable of being linked together and controlled simultaneously. Each video/audio window shall be capable of performing an instant replay of selected duration by simply using a slider control to move back in time. If audio is associated with the selected window there shall be a set of controls to adjust the volume or mute the audio.

- s.	Video Zoom/Full Screen Display

- The currently selected video window shall support digital zooming of 50 percent to 200 percent using pre-defined buttons. As well, wire frame selection of area to zoom shall also be supported with the ability to pan to areas of interest that are outside of the displayed window frame. The displayed video shall have an option to adjust to the size of the window frame. Multiple windows shall be capable of having the zoom and fit-to-screen operations applied simultaneously. Any single video window shall be capable of being displayed in full screen mode with no window frame (audio will continue to be heard in this mode).

- t.	PTZ control

- 1.	The NVR unit shall allow for connection to PTZ cameras through the RS- 232 or RS-485 ports on the unit, and multiple PTZ cameras may be ‘daisy- chained’ on a single port as defined by the PTZ protocol the user deploys (see #2 below). Control of these cameras shall be possible on the operator side through a physical connection to a PTZ controller (keypad/joystick) or through on-screen software controls. On-screen software controls shall allow for selection of PTZ camera to control, direction of camera movement, zoom, focus and configuration of camera preset locations

- 2.	At a minimum, the following PTZ camera protocols shall be supported on the NVR:

- •	Kalatel® KTD-312

- •	Panasonic® WV-CS850

- •	Pelco® D

- •	Pelco® P

- •	Phillips® TC700/TC8560

- •	RVision®

- •	Sony® UniDome UNI-TR1

- •	Ultrak® KD-6

- u.	Video Image Settings

- The video window shall support image controls for brightness, contrast, saturation, and hue levels to customize the appearance of video in the active display window. Recorded video is in no way altered by these controls, however, printed or saved still images can be image enhanced.

- v.	Data ports

- The NVR unit shall be able to capture and store banking ATM/Teller or retail Point-of-Sale (POS) transaction information using the RS-232 data port available on the unit. The text information captured from a transaction system shall not overlay or obstruct the video in any way, but shall be synchronized with that video, and shall serve as a trigger to capture recorded video of preset duration (including pre-transaction video).

- w.	Switch Control

- The NVR viewer shall be able to manually control devices connected to the switch output of the NVR unit by activating one either normally open (NO) or normally closed (NC) contact. The switch shall automatically reset after a configurable period of time. The switch shall also be set in response to an external event occurring or as a scheduled operation.

- x.	Alarm Notification

- The NVR unit shall distribute notification of alarms to clients who have requested notification. All video associated with the alarm shall be automatically displayed on receipt of an alarm. Audible and visual alarm cues shall also be optionally configurable. An operator shall be able to have notification of alarms e-mailed to specific users.

- y.	Time Zones

- The NVR unit shall be capable of operating in a different time zone than a viewing application. The operator shall be able to work in either the time zone of their PC or the time zone of the NVR when searching for video. Operator software shall display either the local (user) time zone, or the time zone of the NVR when displaying video timestamps.

- z.	Search of Alarms

- 1.	Video recorded on alarms shall be searchable by selecting the alarm of interest and entering a specific point in time and period of interest. Each type of alarm shall have a unique icon to represent it in the list. An operator shall be able to narrow down the search without having to re-enter all the parameters. All alarm-associated recordings (i.e. all cameras) shall be retrieved and displayed by selecting a specific entry from the alarm search results. The duration of retrieved video surrounding the alarm point shall be configurable by each user.

- 2.	Video motion alarms shall be handled in the same way as other physical alarms. A mask shall be able to be applied to a search for video motion such that the results list displays only when motion was detected in the area(s) of interest.

- 3.	Transaction events captured from an ATM or bank Teller machine interface shall be handled in the same way as other physical alarms, in that they shall be searchable by date and time as well as other custom user data. The search fields for ATM/Teller transaction alarms shall include:

- •	Transaction type

- •	Transaction number

- •	Transaction amount

- •	Card number

- •	Time/date stamp

- •	Other custom field

- 4.	Transaction events captured from a Point-of-Sale (POS) retail interface shall be handled in the same way as other physical alarms, in that they shall be searchable by date and time as well as other custom user data. The search fields for POS transaction alarms shall include:

- •	Transaction type

- •	Transaction number

- •	Transaction amount

- •	Card number

- •	Time/date stamp

- •	Other custom field

- aa.	Search and Retrieval of Recordings

- 1.	Searching and retrieving video and audio from the NVR unit shall be done as a single operation (i.e. if the audio is associated with the video, it will be retrieved as well).

- 2.	The search function shall allow multiple cameras, multiple NVRs, or multiple NVR locations to be specified and searched simultaneously.

- 3.	Recorded video shall be searchable by:

- •	Selecting the camera of interest and entering a range of times. The user shall be able to further refine this range by a simple “click-and- drag” operation, and not have to re-enter any search parameters. The user shall be presented with a histogram indicating the amount of motion during the time range, as well as a set of thumbnails to aid in pinpointing a time of interest.

- •	Selecting an alarm and using the specific point in time of the alarm to locate the associated video

- •	Using the ‘activity scan’ feature to search based on motion detection

- •	Specifying ATM or POS transaction data as mentioned above

- 4.	The search function shall allow any duration of video to be retrieved (to a maximum file size of 2.0 GB).

- bb.	Playback Viewing

- The retrieved video shall be displayed automatically in a window. The playback windows shall be capable of being displayed alongside the live video windows. If audio is associated with the video that is retrieved, it shall be automatically played when the video is played. A date/time stamp shall appear with the video being displayed and shall be updated for each frame that is displayed.

- cc.	Playback Controls

- 1.	When a playback window is selected, the following controls shall be made available to control the playback of the video:

- •	Play – forward and reverse

- •	Pause

- •	Single frame – forward and reverse.

- •	Move to beginning to ending of video segment

- 2.	In addition, the play speed shall be capable of being changed to 1x, 2x, and 4x normal speed. The recorded video shall also be capable of being quickly navigated using a shuttle search (slide bar). Video frames shall be displayed while the slide bar is being moved to assist in finding the frame of interest.

- dd.	Time Ruler

- For navigation through a video clip, the operator shall be able to use a slide bar. The video image shall update while the slide bar is being moved. To change the time resolution for more accurate navigation, the time ruler shall be capable of being zoomed in or out.

- ee.	Video Images - Copy, Save and Print

- An image from a live or playback video window shall be capable of being manipulated as follows:

- 1.	The image shall be capable of being copied to the PC ‘clipboard’ and then pasted into any third party application that will accept data from that clipboard. These applications include image enhancement, email, or word processing. Image copying options shall include specifying standard JPEG or .BMP file formats for the image. The copied information shall include both video and associated detail data (location, camera, time, date, and event information).

- 2.	The resulting images shall then be able to be saved to the local PC or other network storage location, retaining their JPEG or .BMP file formats and their associated detail data.

- 3.	The images shall also be capable of being printed to any network- connected printer. The printed image shall have the associated detail data (location, camera, time, and date) printed on the same page.

- ff.	Video Clips – Security Sealed

- A video clip from a live or playback video window shall be capable of being controlled as follows:

- 1.	The video clip shall be capable of being saved to the local PC or other network storage location in an industry-standard .AVI read-only file format. The captured information shall include the video clip itself, any audio data if recorded, and associated location, camera, time, date and event details, as well as any captured POS or ATM transaction data.

- 2.	All video clips shall have a tamper-proof security seal applied automatically as part of this process, ensuring the authenticity of that video and its admissibility as evidence in a legal investigation or prosecution process. This security seal process shall be based on the SHA (Secure Hash Algorithm) of Digital Signature Standard [U.S. FIPS PUB 180-1, 1995].

- 3.	Video clips shall be able to be exported from the NVR to a USB-connected CD Burner or memory stick. Control of this operation shall be made available to authorized clients locally or remotely over the network. This export process shall include the copying of a free, auto-run Evidence Reviewer utility with which third parties may play back the video clip. Users of the Evidence Reviewer utility shall have the ability to run the utility directly from the media, without requiring them to install it on their workstations.

- 4.	The industry-standard .AVI video files shall be capable of being displayed by any commercial application that will render such media files. To display all associated detail data, and to verify authenticity of the video, the Evidence Reviewer utility shall be necessary.

- •	PUBLIC LCD DISPLAY:-

- 1.	LCD Screen Size 40"

- 2.	Display Resolution Full HD 1080 (1920 x 1080)

- 3.	Screen Format TV: Full / Normal/ Wide Zoom/ Zoom, PC: Normal/ Full 1/ Full 2

- 4.	Terminals

- •	HDMI / Audio In 2 (1 Rear/ 1 Side)

- •	Component / Audio in 1 (Rear, Composite Input Common Use)

- •	Composite / Audio In 1 (Rear, Composite Input Common Use)

- •	9.2.5 HIGH PERFORMANCE MONITORING PC:-

- Processor: Intel® Core i7-10th Generation

- Memory: 16 Gb (2x8 Gb) DDR4 – 3000 Mhz

- 3.  Hard Drive: 1000GB SSD

- Graphics Card: 8GB NVIDIA GeForce or equivalent (DVI, VGA, HDMI)

- Optical Drive: DVD/CDRW Combo

- Ethernet Interface: Integrated Intel® 82578DM GbE Ethernet LAN 10/100/1000

- Power Supply: 500W Standard

الاعمال الميكانيكية:

  - عام:

- جميع الأعمال الصحية والميكانيكيه للمشروع مبينة على المخططات المعدة لذلك وحسب تعليمات المهندس المشرف.

    - إضافة إلى قواعد الكيل وشمولية الأسعار الواردة للبنود المختلفة من المواصفات الفنية العامة للمباني المجلد الثاني-الخدمات الميكانيكية للمباني ، تعتبر الأسعار التي يحددها المقاول لقاء كل بند من بنود جدول كميات الأعمال الميكانيكية وعلى سبيل المثال لا الحصر شاملة لما يلي:-

    - تنفذ أعمال هذا القسم وفقاً لمواصفات الخدمات الميكانيكية للمباني- المجلد الثاني - من المواصفات الفنية العامة للمباني،  بالإضافة إلى أية أبواب أخرى من أبواب المواصفات وله علاقة بهذا العمل.

    - في حال عدم تغطية المواصفات في البند السابق لبعض الأعمال فيتم تنفيذها طبقا للمواصفات البريطانية (B.S) أو ما يعادلها.

    - تتقدم قواعد الكيل وشمولية الأسعار الواردة في جدول الكميات اللاحق على مثيلاتها في المواصفات الفنية العامة ويؤخذ بها وتعتمد ولا تعتبر متناقضة معها.

    - جميع الأعمال والمواد والتجهيزات وطريقة التنفيذ خاضعة لموافقة المهندس المستشار.

    - تعتبر الأسعار الفردية شاملة تقديم المواد وتركيبها وتشغيلها وصيانتها في أي موقع ومنسوب من المشروع لتصبح جاهزة تعمل حسب الحاجة الموجودة من أجلها.

    - على المقاول تقديم مخططات تنفيذية (Shop Drawings) شاملة التفاصيل الفنية والمعلومات والكتالوجات كاملة والعينات وحسب ما يطلبه المهندس المستشار وكذلك المخططات حسب التنفيذ (As Built Drawings).

TECHNICAL SPECIFICATION

MECHANICAL SERVICES

##### TABLE OF CONTENTS

| Section No. | Title |
| --- | --- |
| 15010 | Basic Mechanical Requirements |
| 15171 | Electrical Requirements for Mechanical Equipment |
| 15185 | Hydronic Pumps |
| 15190 | Mechanical Identification |
| 15195 | LPG Gas Piping |
| 15210 | Equipment Bases, Supports and Vibration Isolation |
| 15291 | HVAC thermal Insulation |
| 15310 | Fire Protection System |
| 15410 | Plumbing Piping |
| 15411 | Plumbing Valves |
| 15412 | Plumbing Supports, Hangers and Brackets |
| 15430 | Plumbing Specialties |
| 15440 | Plumbing Fixtures |
| 15443 | Solar Flat Plate Collectors |
| 15444 | Packaged Booster Pump Set |
| 15452 | Tanks |
| 15471 | Potable water treatment and filtration equipment |
| 15487 | Domestic Hot Water Storage Heaters (Calorifiers) |
| 15500 | Heating, Ventilation and Air Conditioning |
| 15513 | HVAC Noise Control |

| Section No. | Title |
| --- | --- |
| 15856 | Air Movers: Centrifugal And Axial |
| 15890 | Ductwork |
| 15910 | Ductwork Accessories |
| 15940 | Air Outlets and Inlets |
| 15996 | HVAC Testing, Adjusting, and Balancing |

| DIVISION – 15 MECHANICAL SECTION – 15010 | TECHNICAL SPECIFICATION MECHANICAL WORK ## BASIC MECHANICAL REQUIREMENTS |
| --- | --- |

# PART 1 GENERAL

1.01	SCOPE OF WORK

This Section covers the basic general requirements applicable to all Division 15 works that shall be provided for by the Contractor.

1.02	CALCULATIONS

A.	The Contractor shall acquaint himself with the constructional details of the buildings and exterior works both before and during the course of erection and shall take his own particulars with regard to the installation of mechanical equipment.  The Contractor shall check the sizes of all mechanical equipment taking into account any additions or deletions required to ensure the installations fit into the room or other spaces allocated and in relation to other plant and equipment being provided.

B.	The Contractor shall undertake and prepare all necessary calculations and drawings relating to the mechanical equipment and for all associated foundation, structural and builder's and services work, except where specifically defined otherwise in the Specification and/or on the Drawing.

C.	The Contractor shall provide and submit to the Engineer all calculations, drawings and supporting data for the mechanical equipment.

D.	The Contractor shall provide calculations, details, drawings and technical data to enable the Engineer to ascertain the correctness of the specialist designs of the associated foundations, supports, bases and fixings.

1.03	WORKING DRAWINGS

A.	The Contractor shall provide for approval working drawings of the whole mechanical works.  The drawings shall include, but not necessarily be limited to the followings: -

1.	Co-ordinated general arrangements of all services to a scale of not less than 1:100

2.	Co-ordinated detailed layouts of plant rooms and similar spaces to a scale of not less than 1:50.

3.	Schedules of all equipments to be installed, together with start and running power consumption.

4.	Indicate with accurate dimensions sizes and positions of all plant, equipment, pipes, conduits, trunking, underfloor ducting, cable tray, cables together with all inspection points and cable joints.

5.	Fully indicate all ductwork, pipework, sizes and positions of all plant equipments and valves together with all inspection points and test positions.

6.	Fully indicate all builder's work requirements inclusive of all foundations, bases, plinths, sumps and holes together with the overall sizes and masses of the plant concerned.

7.	Show the disposition and depth of all cables, pipes, ducts, buried direct in the ground and taken at intervals where change of direction occur and where cables increase or decrease in number/size and at every point where the services enter into or depart form ducts or buildings.

8.	Indicate the number, size and services for every cable, ducts, pipes for every service within the building.  Circuit lists for every distribution board shall be entered onto the relevant drawings and such lists shall agree with the lists fixed within the distribution board door.

9.	Indicate all equipment and control wiring diagrams together with all specialist systems.

10.	Show all cables in pits and ducts on drawings to a scale of 1:50 or larger.

11.	Show clearly on site drawing all the new buildings together with all other existing buildings and other permanent features and dimensions between such buildings and cables, pipes, ducts, etc. clearly marked.

12.	Show clearly all plumbing and drainage and setting out dimensions for all drainage pipework and manholes, both within the building and throughout.

13.	The site, together with intended drainage pipework backfill, or surround in each location, schedule to be included to indicate manhole, and cover size, etc.

B.	The symbols used for each service for all working drawings shall be shown on separate drawings.

C.	In addition to the working drawings, the Contractor shall obtain and provide at the request of the Engineer, two sets of all manufacturer's detailed drawings for all items of plant, equipment, apparatus and materials.  These drawings shall be suitably titled and have drawings references number added. Specific requirements are given in the individual specification Sections.

D.	All drawings, diagrams and schedules called for in this clause shall be submitted to the Engineer for examination and approval.

E.	The Contractor shall make due allowance for an approval/comment period and it must be clearly understood that the correctness of the submitted information will directly affect this comment/approval period.

F.	The Contractor shall be responsible for co-ordinating all mechanical, electrical, fire protection plumbing, drainage condensate, and irrigation works, and engineering systems such that each may be installed in a proper manner, ensuring correct performance and allowing adequate maintenance access.  All services shall be installed such that the positioning of ducts, pipes, cables, and all items of equipment avoid conflict.  The Contractor's working drawings shall indicate any services co-ordination needs prior to submission to the Engineer for approval; tender drawing shall not be reissued as working drawings.

1.04	CONSTRUCTION DRAWINGS

A.	Following approval of the Contractor's drawings by the Engineer, they shall constitute "Construction Drawings" and the E and M equipment shall be manufactured and installed in accordance with those approved drawings.  The acceptance by the Engineer of any such drawing shall not relieve the Contractor of his responsibility under the Contract and shall not commit the Engineer or make the Engineer liable for any mistake of the manufacturer's deficiencies in strength or efficiency in operation of any part of any item for its specified purpose.

B.	The Engineer reserves the right subsequently to amend or add to the Construction Drawings as may be necessary or expedient.

C.	The Contractor shall provide to the Engineer, immediately after approval of each detailed drawing, one copy on transparent plastic film and two dye-line prints.

1.05	REGULATIONS

A.	The installation materials and components shall comply with all relevant statutory instructions and regulations current at the date of tender, whether so detailed or not.  In particular, the following departments must be consulted.

1.        Jordanian Uniform Plumbing Code.

2.	British Standard Specifications

3.	British Standard Code of Practice

4.	UK IEE Regulations for Electrical Installation

5.	US National Electrical Code

6.	US National Electrical Safety Code

7.	UK Chartered Institution of Building Services Engineers (CIBSE)

8.	The American Society of Heating, Refrigerating and Air Conditioning Engineers (ASHRAE)

10.	Electrical Regulations issued by Local Authorities.

11.	US Sheet Metal and Air Conditioning Contractors National Association (SMACNA)

12.	UK HVCA DW143 Ductwork specification.

13.	US National Fire Protection Association Standards

14.	IEE Regulations for Electrical Equipment of Buildings

15.	Local Laws, Rules and Regulations

16.	U.K BSRIA code for pipework flushing.

17.	US Air Conditioning and Refrigeration Institute (ARI)

18	US American Society for Testing and Materials (ASTM)

19	US Air Movement and Control Association (AMCA)

- US Underwrites Laboratories (UL)

- MOPWH General Buildings Specifications

- Civil Difence.

1.06	CLIMATIC AND OPERATING CONDITIONS

A.	Country			: Jordan

Elevation		: 700 m above sea level

Temperature    		: See specification clauses.

1.07	WORKMANSHIP AND MATERIALS

A.	The Contractor shall be responsible for ensuring that the components or each system are mutually compatible and integrated to form fully efficient systems complying with the Drawings and Specification.  Corresponding parts throughout the Works shall be made to gauge and be interchangeable wherever possible.  The Contractor shall, when required by the Engineer, prove interchangeability by the actual interchange of the various parts.

B.	All articles and materials specified to conform to Iranian, British and other standards shall be clearly and indelibly marked with the appropriate standard number specified except where marking is impracticable when relevant documents shall include this information.

C.	All materials and workmanship shall be to the satisfaction of the Engineer.  The Contractor shall maintain a competent supervising engineer and supervisors for each specialisation and for each section of the work on Site throughout the whole of the time to the completion of the works.  The Engineer shall give prior approval to the appointment of this supervising engineer and shall have the authority to withdraw this approval at any time.  No person shall be allowed to execute any type of work, which is normally carried out by a skilled tradesman unless he is thoroughly experienced and proficient in the trade concerned.  The Engineer shall have the authority to require any tradesman to demonstrate his proficiency to the satisfaction of the Engineer.

D.	Where "stainless steel" is specified or used it shall have resistance to atmospheric corrosion and be of a grade to suit its particular use.  Particular attention shall be made to the prevention of seizure by fretting where two corrosion resistant metals are in contact, by the selection of materials of suitable relative hardness and surface finish and the applications of lubricants.  Where bronze is specified or used it shall be zinc free.

E.	All cast iron shall be of standard grey close-grained quality to BS 1452 Grade 14 or better.  The structure of the casting shall be homogenous and free from non-metallic inclusions and other injurious defects.  All surfaces of casting which are not machined shall be smooth and shall be carefully fettled to remove all foundry irregularities.

F.	Minor defects not exceeding 12.5% of total metal thickness and which will not ultimately affect the strength and serviceability of the casting may be repaired by approved welding techniques.  The Engineer shall be notified of larger defects and no repair welding of such defects shall be carried out without prior approval.

G.	If the removal of metal for repair will reduce the stress-resisting cross-section of the casting by more than 25%, or to such an extent that the computed stress in the remaining metal exceeds the allowable stress by more than 25%, then that casting may be rejected.

H.	Castings repaired by welding for major defects shall be stressed-relieved after such welding.

J.	Non-destructive tests will be required for any casting containing defects whose extent cannot otherwise be judge, or to determine that repair welds have been properly made.

K.	All major stress-bearing forgings shall be made to a standard specification that shall be submitted to the Engineer for approval before work is commenced.  They shall be subject to internal examination and non-destructive tests for the detection of flaws and shall be heat-treated for the relief of residual stresses.  The name of the maker and particulars of the heat treatment proposed for each such forging shall be submitted to the Engineer.  The Engineer may arrange for such forgings to be inspected at the place of manufacture with a representative of the Contractor.

L.	Particular attention shall be paid to the prevention of corrosion due to the close proximity of dissimilar metals.  Where it is necessary to use dissimilar metals in contact, they shall be selected so that the bimetallic corrosion is as low as possible.  The publication by the UK H.M. Stationary Office entitled "Corrosion and its Prevention at Bimetallic Contacts" shall be used as a guide.

M.	The use of iron and steel shall be avoided in instruments and electrical relays wherever possible.  Steel screws, when used, shall be zinc, cadmium or chromium plated or, when plating is not possible owing to tolerance limitations, shall be of corrosion resisting steel.  All woodscrews shall be of dull nickel-plated brass or of other approved finish.  Instrument screws (except those forming part of a magnetic circuit) shall be of brass or bronze.  Spring shall be of non-rusting material, e.g., phosphor bronze or nickel silver, as far as possible.  Pivots and other parts of which non-ferrous material is unsuitable shall be of approved rustless steel where possible.

1.08	INSPECTION AND TESTS AT MANUFACTURER'S WORK

A.	The Engineer and his duly authorized representative shall have at all reasonable times access to the Contractor's premises to inspect and examine the materials and workmanship of mechanical equipment being manufactured there, and if part of such equipment is being manufactured on other premises, the Contractors shall obtain for the Engineer and for his duly authorized representative permission to inspect as if that equipment was manufactured on the Contractor's own premises.  Such inspection, examination or testing, if made, shall not relieve the Contractor from any obligation under the Contract.

B.	All works, materials and the like rejected shall be corrected or replaced as necessary at the Contractor's own expense to the satisfaction of the Engineer.

C.	Where the mechanical equipment is composite unit of several individual pieces manufactured in different places, it shall be assembled and tested as one complete working unit, at the manufacturer's works, to the relevant test or tests required.

D.	The Contractor shall submit his proposed program of tests for the Engineer' approval six weeks before the commencement of testing.

E.	The aforementioned works tests carried out before delivery to the Site shall not in any way relieve the Contractor of completing satisfactory Site tests after erection as specified.

F.	The Contractor shall give the Engineer reasonable notice, at least ten clear days in writing, of the date and the place at which any mechanical Equipment will be ready for testing as provided in the Contract and the Engineer shall thereupon at his discretion notify the Contractor of his intention either to release such part upon receipt of works tests certificates or of his intention to inspect such part.  The Contractor shall forward to the Engineer six duly certified copies of all relevant test readings.

G.	The Contractor shall provide, free of charge, such labour, materials, electricity, fuel, water, stores, apparatus, instruments and other things as may be reasonably demanded to carry out efficiently such tests of the mechanical equipment in accordance with the Contract, and shall provide facilities to the Engineer or to his authorized representative to accomplish such testing.  Where inspection or testing is to be carried out at a Sub-contractor's works, a representative of the Contractor shall be present.

H.	Works tests shall also be carried out such that due consideration is given to the Site conditions under which the mechanical equipment is required to function.  The tests certificates shall give all details of such tests.

I.	Specific performance works tests are described in the relevant Sections of Division 15, and include:

a)	Sample performance testing of split units for airflow, heating and cooling & and noise emission.

1.09	CERTIFIED DRAWINGS

A.	The Contractor shall be responsible for providing all "Certified" drawings from manufacturers of mechanical equipment, prior to their manufacture and installation.  A "Certified' manufacturer's drawing shall mean a drawing which is prepared by a manufacturer as showing the exact dimensions and details of items of the mechanical equipment, as they will be supplied and installed in the Works.

1.10	SAMPLES

A.	The Contractors shall provided a sample properly labelled of all fittings, valves, insulation, cocks, unions, grilles, dampers, switchgear, cables and other like accessories described in the Specification or as required by the Engineer.

1.11	PROTECTION AND CARE OF PLANT AND EQUIPMENT

A.	All mechanical equipment shall be packed in robust containers to prevent damage and mishandling during transport to Site.  Before dispatch from works all mechanical equipment shall be thoroughly cleaned, protected against damage, deterioration, corrosion and ingress of dirt and packed and protected suitable for prolonged storage in a humid and saline atmosphere.

During storage and erection at the Site, the mechanical equipment shall be kept clean and free from dirt and debris, and water shall not be allowed to remain in any pockets of the equipment.  All items of mechanical equipment shall be stored clear to the ground on suitable timbers to the approval of the Engineer.

All mechanical equipment, particularly electrical and other sensitive instrumentation shall at all times be protected so that it is not subject to damage by rainwater, moisture, dust, etc., from any source.  Mechanical equipment which may be damaged by heat or sun shall be protected accordingly.  All open piped ends and duct ends whether installed or in store shall be fitted with plastic caps or suitable protective covering.

1.12	GUARDS

A.	A guard shall be provided for all open unprotected intakes to axial fans, centrifugal flow fans, for V-belt drives or in any position required by the UK Factories Act.

Fan guards shall be made of galvanized steel wire mesh, not greater than 25mm attached to a rigid galvanized steel rod framework. The fan maker shall manufacture the fan guards.

Cleaning:  The Contractor shall be responsible for cleaning all mechanical equipment at all times to the satisfaction of the Engineer.  The cleaning shall be carried out notwithstanding the fact that the installation or any part thereof may be in use of partial use within the premises in occupation by others.  A Certificate of Completion will not be issued until the Engineer is satisfied that all dirt, jointing materials and other extraneous and injurious materials have been removed.

1.13	AIR CONDITIONED STORES

A.	The Contractor shall provide air-conditioned site stores for all goods that deteriorate when subjected to the site climatic conditions detailed. The contractor will adhere strictly to the Manufacturer's instructions with regard to storage temperatures for all materials being used for the construction of this project.

1.14	PAINTING

A.	The preparation, painting and treatment of mechanical equipment surfaces shall be in accordance with relevant items in Division 15.

B.	Full details of the manufacturer's standard finishes shall be given to the Engineer for his approval prior to manufacturer.  Special care shall be taken to ensure standard finishes are suitable for the particular conditions applicable to the individual items of plant.

C.	Any damage to paintwork occurs shall be made good by the Contractor at his own cost to the satisfaction of the Engineer.

D.	The interiors of control panels shall be finished white enamel paint (two coats) and shall comply with the appropriate BS for enamel finish and the exteriors of such panels shall be of BS Specification colour as specified by the Engineer to give a minimum reflection value of 42%.  Instruments shall be finished dull black and control handles, push button and similar fittings shall be chromium plated or otherwise durably finished to the approval of the Engineer.

E.	All bright metal parts shall be covered before despatch with an approved protective compound and protected adequately during delivery to Site.  After erection these parts shall be cleaned with a correct solvent and polished bright where required.

F.	Machined mating surfaces such as gear teeth, etc., shall be coated with a thick layer of grease.  Other machined surfaces shall be given a coat of rust-preventing paint that shall be readily removable when required.

G.	Where it is the usual practice of the manufacturer of special items such as pumps, compressors, electric motors, gear boxes, switch gear, etc., to apply a high standard of protective enamel paintwork in the shops before dispatch, this will be acceptable provided any subsequent damage to the paintwork is made good by the Contractor, at his own cost.  The preferred finish is light grey.

H.	The inside of outdoor control cubicles, cabinets, etc., where condensation is liable to occur, shall be coated with an approved anti-condensation composition.

J.	The Contractor shall obtain the paint manufacturer's guarantee that each coat of paint is compatible with the previous and subsequent coats so that peeling, flaking and other faults do not occur.

K.	The Contractor shall include for painting all pipes, ducts, flange edges, etc., prior to their being insulated.

L.	Final decoration of exposed pipework, brackets and ductwork shall be carried out in accordance with standards.

1.15	MANUFACTURER'S NAMEPLATES

A.	Nameplates:  Each item of mechanical equipment and plant shall have the manufacturer's name or trademark on a corrosion-resistant nameplate securely affixed in a conspicuous place.  The manufacturer's name or trademark may be cast integrally with stamped or otherwise permanently marked upon the item of the equipment.  The nameplate shall show the equipment reference number, date of manufacture and the capacity.  Such other information as the manufacturer may consider necessary to complete identification shall be shown on the nameplates.

1.16	LABELS

A.	Identification labels of plastic laminate or similar approved materials engraved black on white unless otherwise agreed, with not less than 5mm "line" style letters shall be fixed on or adjacent to all controls, switches and distribution gear, by means of at least two brass screws.  Socket outlets of all voltages shall be similarly identified or engraved.

B.	The labels shall bear the identification shown on the Drawings, such as indication, designation, function and, where necessary, phase, voltage, current, frequency, pressure and temperature.  All labels shall be in Arabic and English.

1.17	LUBRICATION

A.	A complete schedule of recommended oils and other lubricants shall be furnished by the Contractor.  The number of different types of lubricants shall be kept to a minimum.   The schedule and the name of the supplier of the lubricants shall be submitted to the Engineer for approval before incorporation in the instruction manuals.  In the case of grease lubricated roller type bearings for electric motors, a lithium base grease is preferred.

B.	Where lubrication is affected by means of grease, preference shall be given to a pressure system, which does not require frequent adjustment or recharging.  Frequent for this purpose, means more than once weekly and grease systems having shorter periods between greasing should be avoided.  Where necessary for accessibility, grease nipples shall be placed at the end of extension piping and, when a number of such points can be grouped conveniently, the nipples shall be brought to a battery plate mounted in a convenient position.  Button head type nipples shall be of the same size and type for every part of the plant.  Arrangements shall be provided to prevent bearings being overfilled with either grease or oil

C.	Where more than one special grease is required a grease gun for each special type shall be supplied and permanently labelled.

D.	Oil sumps shall be fitted with oil level indicators of the sight glass type, or where this is not practical, with dipsticks.  The indicators shall show the level of all temperatures likely to be experienced in service.  The normal, maximum and minimum levels at 30oC shall be clearly visible in the sight glass type from the normal access floor to the particular item of plant, and they shall be easily dismantled.

E.	All sight glasses shall be firmly held and enclosed in metal protection in such a manner that they cannot be accidentally damaged.

F.	All lubrication systems shall be designed so as not to present a fire hazard and particular care shall be taken to prevent leakage of lubricants and to avoid leaking lubricants coming into current contact with any electrical equipment, heated surfaces or any other potential source of fire.

G.	The Contractor shall supply flushing oil for each lubrication system when an item of plant is ready for preliminary running and a sufficient quantity of the approved lubricants for setting to work and for the commercial operation for one year after the relevant Certification of Completion has been issued.

1.18	SPECIAL TOOLS

A.	The Contractor shall supply two complete sets of any special tools necessary for the operation, maintenance and dismantling of the mechanical equipment.  The Contractor shall supply wall-mounted strongboxes, each fitted with a suitable lock and two keys, and located near the item of mechanical equipment for which they will be used.  The Contractor shall not use such tools during the erection of the mechanical equipment.

1.19	SUNDRY BUILDERS WORK IN CONNECTION WITH SERVICES

A.	The Contractor shall include in his prices for drilling, rawbolting, plugging, screwing and nailing of all brackets, hangers, for all pipework, ductwork conduit, cable tray, cable trunking and cable supports.  The Contractor shall also include for supplying all brackets, hangers and supports as necessary.

1.20	NOISE

A.	The Contractor shall provide a quiet installation.  All items of mechanical equipment shown on the Drawings shall be carefully chosen with a view to silent operation.  The recommendations in BS 5720 and BSCP 3 Chapter III shall be followed wherever necessary.  The Contractor shall prepare detailed noise level calculations to indicate the anticipated noise levels in all critical areas.

B.	All possible steps shall be taken, (e.g. by the use of sound insulation, anti-vibration mountings, and careful design of motors, fans, ducts, bends, dampers, grilles and other equipment) to reduce the noise produced by the mechanical equipment.

C.	The Contractor shall determine the noise levels of all primary mechanical equipments before proceeding with manufacture and submit sound power levels of such Equipment to the Engineer for approval before manufacture is commenced.

1.21	ANTI-VIBRATION MOUNTINGS AND SOUND ABSORPTION

A.	The Contractor shall provide and fix all mechanical equipment to prevent noise and the transmission of vibration through the structures.

B.	All fans, motors, compressors and other items, as appropriate, shall be mounted on resilient mountings in such a manner that the plant foundations are isolated from the floor or structure.  In addition, all rotating plant shall be statically and dynamically balanced.

C.	Mechanical vibration shall be eliminated by the use of anti-vibration mountings and flexible connections to ensure an isolation efficiency of 95% from the building structure except where defined otherwise on the Drawings or in the Specification.

D.	Spring type anti-vibration mountings shall be the captive partially encased and restrained type to prevent lateral movement.

1.22	AS BUILT DRAWINGS

A.	Thirty days prior to the date of the handing over certificate, the Contractor shall provide for approval "as built" record drawings of the whole works.

B.	The Drawings shall include the following:-

1.	General arrangements of all services to a scale of not less than 1:50.

2.	Detailed layouts of plantrooms and similar spaces to a scale of not less than 1:20.

3.	Schedules of all plant and crossed referenced equipment to the maintenance manual.

4.	All equipment and control wiring diagrams together with specialist system i.e. public address, fire alarms, etc.

5.	These may be produced separately or included with the general distribution diagrams.

6.	Indicate with accurate dimensions, sizes and positions of all plant, equipment and valves together with all inspection points and test positions.  All plants to have indicated manufacturer's name, model and type number also cross referenced to maintenance manual.

7.	Fully indicate all ductwork, pipework, sizes and positions of all plant equipment and valves together with all inspection points and test positions.  All plant to have indicated manufacturer's name model and type number also cross referenced to maintenance manual.

8.	Show the disposition and depth of all cables, pipes, ducts, buried direct in the ground and taken at intervals where cable increase or decrease in number/size and at every point where the services enter into or depart from ducts or buildings.

9.	Indicate the number, sizes and services for every cable, duct, pipe, for every service within each building.  Circuit lists for every distribution board shall be entered on to the relevant drawings and such lists shall agree with the list fixed within the distribution board door.

10.	Show clearly on site drawings all the new buildings together with all other existing buildings and other permanent features with dimensions between such buildings and cables, pipes, ducts, etc. clearly marked, together with installed backfill and surround to each services.

11.	Indicate all equipment and control wiring diagrams together with all specialist systems i.e. public address, fire alarm, etc.  Diagrams must be co-ordinated and show all required interblocks etc. between systems or components.

12.	Show clearly all plumbing and drainage and setting out dimensions for all drainage pipework and manholes both within the building throughout the site, together with drainage pipework backfill, or surround in each location.  A schedule shall be included to indicate each manhole size, cover size, invert level and ground level.

C.	The symbol used for each service for all as built drawings shall be shown on separate drawings.

D.	In order to achieved accurate as built drawings, all relevant information relating to the mechanical works shall be entered onto prints supplied immediately after the work has been carried out.  The marked up prints shall be available for inspection at the Contractor's site office at any reasonable time during the progress of the works.

E.	All service routes, intersections and joints shown on the prints and finally recorded shall be actually physically measured from permanent features and accurate distances shall be shown on the Drawings.

F.	In addition to the as built drawings, the Contractor shall obtain and provide two sets of all manufacturer's detailed drawings for all items of plant, equipment, apparatus and materials.  These drawings shall be suitably titled and have drawing reference numbers added.

G.	The Contractor shall provide two copies for all as built drawings for review comments and approval.  Upon receiving approval in writing from the Engineer, or his representative, the Contractor shall provide one negative copy of each approved as built drawing and bind one set of prints into each of 6 No. copies of the operating instructions specified in clause 1.23.

1.23	OPERATING AND MAINTENANCE INSTRUCTIONS

A.	The working, operating and maintenance instruction shall be prepared in draft as soon as the working drawings are in hand and shall take the form of a manual in which fully detailed information relating to the maintenance and operation of the complete installation and its component parts is presented.

a)	Overall general description of the complete equipment installed together with the method of functioning.

b)	Full technical descriptions of each and every item of equipment, including the electrical circuit details as applicable.

c)	Operating procedures for each section of the works and each individual item of equipment or plant.

d)	Planned maintenance schedules for the installation and its component parts to include commissioning performance details and measurements.

e)	Schedule of components comprising each and every item of equipment including manufacturer's name, description and part number of each component.

f)	A copy of the manufacturer's literature, describing each item of equipment, plant fittings and accessory type used throughout the installation.  This literature shall list the technical data available, together with catalogue list numbers for replacement purposes.

g)	Generally all drawings must be arranged to flood out from their position and be entirely visible when any part of the manual is being read.  They shall be printed on linen backed paper.

h)	Each section shall be encased in a loose leaf ring binder covered in plastic material of an approved colour and of a type which shall be flat when open.

i)	The Contractor shall include for the preparation and supply of six copies of the above operating and maintenance instructions for each section after all details have been approved by the Engineer.

j)	Electric transfer of "As Built" drawings shall be provided as required by the Engineer.

1.24	INSTRUCTION AND TRAINING

The Contractor shall be responsible for the provision of suitably qualified personnel for the instruction and supervision of the Employer's staff at Site in the operation and routine maintenance of all mechanical equipment and associate works.  Unless specified to the contrary in the specific technical clauses in Division 15 instruction and training shall be for periods of six hours daily for two days after the satisfactory commissioning of the installation and as necessary, after each subsequent commissioning of a system or part thereof.

1.25	SPARES AND CONSUMABLES

A.	A list of spares and consumables for 1 years operation for every item of plant and system shall be furnished by the Contractor at the time of tendering.

1.26	MOCK-UPS

- The Contractor shall provide mechanical equipment to allow full Architectural Mock-ups to be built as described elsewhere in the specification.

1.27	Fire stopping material

“All mechanical and electrical penetrations passing through walls, floors and

ceiling must be sealed by appropriate fire stopping material. The product shall

exhibit the minimum designed fire resistant properties when tested as per ASTM

E-814, ASTM G21, UL 1479 or UL 2079 and shall withstand the effect of

earthquake motion”.

1.28	Warranties

- All warranties for mechanical equipment shall start from the date of taking over certificate.

- General Warranty: The special warranty specified in this specification shall not deprive the Owner of other rights the Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by the Contractor under requirements of the Contract Documents.

# PART 2  PRODUCTS

2.01	Not Used.

# PART 3  EXECUTION

3.01	Not Used.

END OF SECTION 15010

| DIVISION – 15 MECHANICAL # SECTION – 15171 | TECHNICAL SPECIFICATION MECHANICAL WORK ELECTRICAL REQUIREMENTS FOR MECHANICAL EQUIPMENT |
| --- | --- |

# PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This Technical Specification details the electrical requirements of the mechanical equipment and plant.

B.	All electrical materials, equipment, plant and installation procedures shall be in accordance with Division 16 of this Specification.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour materials and the performance of all operations in connection with the electrical requirements for mechanical equipment.

B.	Co-ordination:  The Contractor shall be responsible for the full co-ordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	The Contractor shall employ specialist electrical equipment installers and manufacturers that can demonstrate at least 5 years successful experience in the supply and installation of the type of equipment and systems specified.

1.04	APPLICABLE CODES AND STANDARDS

A.	The Electrical Requirements shall comply with the latest relevant British Standards in all respects.

B.	The following are some of the most commonly used British and other Standards associated with Electrical works. However, the Contractor shall ensure all applicable Standards are complied with, whether listed here or not.

BS 1376	-	Specification for colours of light signals.

BS 2757	-	Method for determining the thermal classification of electrical insulation.

BS 4099	-	Colours of indicator lights, push buttons, annunciators and digital readouts.

BS 4794	-	Special requirements for specific types of control

Part 2			switches.

BS 6231	-	Specification for PVC insulated cable for switchgear and controlgear wiring.

IEC 144	-	-	Degrees of protection of enclosures for low voltage switchgear & controlgear.

1.05	SUBMITTALS

A.	Drawings refer to 15010

B.	Product data - relating to each and every component and assembly.

C.	Systems information - full schematic and wiring diagrams including panel fascia layouts.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with 15010

1.07	WARRANTY

A.	Provide 12 months warranty in accordance with contract conditions.

1.08	EXTRA MATERIALS

A.	Comply Section 15010.

# PART 2 PRODUCTS

2.01	CONTROL PANEL ENCLOSURES

A.	Panels shall be constructed from 2 mm thick galvanized steel plate to IP54.

B.	Each composite panel shall include a main isolator interlocked with the door that shall be lockable. All panels shall be finished with stove enamel internally and externally. All panels shall be sealed against ingress of moisture, dust and vermin. All starters and controls shall be located in panels unless agreed otherwise by the Engineer.

C.	An earthing bar shall be provided throughout the entire length of the control panel.

D.	A minimum of 2 doors shall be provided on any panels wider than 800 mm that shall be fabricated to form rigid trays with dust excluding gaskets around their perimeter.

Doors shall be filled with hinges to facilitate the removal of the door panels if required.

All doors shall be interlocked or arranged such that the door that provides access to the main isolator must  be opened first.  All door locks shall be provided with common keys.

2.02	CONTROL SWITCHES AND ELECTRICAL ISOLATION

A.	Control switches shall comply with BS 4794.

B.	Switches shall be of the rotary type.

C.	All control switches shall be capable of being locked in the "off" position, unless stated otherwise.

D.	The contacts of all switches shall be strong and have a positive wiping action when operated.

E.	All control switches shall be provided with labels.

F.	All control panels shall be provided with a defeat proof door interlock isolator controlling the main incoming supply.  The isolator shall be capable of making and breaking on full load without damage.  Additionally the isolator shall have:-

a)	Auxiliary contacts to isolate any secondary supplies to the control panel.

b)	Manual override switch to enable the control system only to be energised whilst the incoming supplies are isolated.

All terminals of the isolator (incoming and outgoing) are to be shrouded to prevent accidental contact.

G.	The panel shall be constructed such that power (3 phase and single phase) equipment is located behind the interlocked isolator door.

Control (extra low voltage) equipment shall be located behind the second or subsequent doors to ensure segregation from power equipment.

The control system operating voltage shall not exceed 220V without prior authorisation.

All internal wiring shall be enclosed within wireways.  Inter wiring that is required to pass between the power and control sections of the panel shall be enclosed within separate or segregated wireways to ensure electrical separation of the power and control systems.

2.03	INDICATING LAMPS INSTRUMENTS AND FITTINGS

A.	Indicating lamps fitted into the facias of switch and instrument cubicles or panels shall be adequately ventilated.

B.	A red warning light shall be provided to indicate "Main Supply On".

C.	The following must be included on all local HVAC control panels (EMCP's and MCP's).

a)	Run/trip lamps for all equipment to prevent accidental contact.

D.	The following must be included on all local HVAC control panels (EMCP's and MCP's).

a)	Run/trip lamps for all equipment

b)	Panel live lamp

c)	Rotary switches for all single plant items

d)	Ammeters for all motors.

e)	Warning lamps

f)	Gauges

g)	Filter clogged indicator lamp.

E.	Lamps shall be easily replaceable from the front of the panel by manual means without the use of extractors.

F.	The bezel of metal or other approved material holding the lamp glass shall be of an approved finish and easily removable from the body of the fitting so as to permit access to the lamp and lamp glass.

G.	The lamps shall be clear and shall fit into a standard form of lamp holder. The rated lamp voltage should be 10 percent in excess of the auxiliary supply voltage, whether ac or dc.

H.	The lamp glasses shall comply with BS 1376 and BS 4099 and shall be in standard colours, red, green, blue, white and amber. The colour shall be in the glasses and not an applied coating and the different coloured glasses shall not be interchangeable. Transparent synthetic materials may be used instead of glass, provided such materials have fast colours and are completely suitable for use in tropical climates.

I.	All indicating 1 Amp circuits shall have a "Test Lamp" switch.

2.04	SMALL WIRING

A.	All control panel wiring shall be carried out in a neat and systematic manner with cable supported clear of the panels and other surfaces at all points to obtain free circulation of air.

B.	In all cases, the sequences of the wiring terminals shall be such that the junction between multi-core cables and the terminals is affected without crossover. Except where terminals are approved by the Engineer for use with bare conductors, crimped connectors of approved type shall be used to terminate all small wiring. Insulating bushes shall be provided where necessary to prevent chafing of wiring.

C.	All panel wiring shall comply with the requirements of BS 6231 Type A or B, as appropriate. Conductors shall be copper and have a minimum cross section equivalent to 50/0.25 mm (2.5 mm²), 7/0.67 mm (2.5 mm²) or 1/1.78 mm (2.5 mm²). 7/0.67 mm shall only be employed for rigid connections which are not subject to movement or vibration during shipment, operation or maintenance. Flexible conductors equivalent to 30/0.25 mm (1.5 mm²) or smaller sizes generally shall only be employed with written approval.

D.	All wires shall be colour coded and fitted with numbered ferrules of approved type at each termination. At points of inter-connection between wiring, where a change of numbering cannot be avoided, double ferrules shall be provided. Such points shall be clearly indicated on the wiring diagram.

E.	No wires shall be teed or jointed between terminal points.

F.	Electrical wiring and instruments shall be located so that leakage of oil or water cannot affect them.

H.	All metallic cases of instruments, control switches, relays etc., mounted on control panels or in cubicles, steel, or otherwise, shall be connected by means of copper conductors of not less than 2.5 sq.mm section to the nearest earth bar. These conductors may be bare or have insulation coloured green/yellow stripes.

2.05	LINKS AND FUSES

A.	Provision shall be made for isolating links to enable circuits to be isolated for maintenance and testing items of plant on the panels without affecting other circuits. These links shall be clearly labelled.

B.	All incoming supply terminals above 220V shall be shrouded.

C.	Fuses of the appropriate rating shall be fitted to each outgoing circuit to provide both overload and short-circuit protection.

D.	All fuses shall be of the HRC cartridge type and comply with BS 88. Carriers and bases for fuses and links shall be coloured in accordance with local practice. The labelling of links and fuses shall be in accordance with the schematic diagrams. A complete set of spare fuses shall be provided in each panel.

E.	If miniature circuit breakers and/or moulded case circuit breakers are utilised in any circuit, and "back-up protection is required to afford adequate discrimination between these circuit breakers and any other protective device in the circuit, HRC fuses shall be used as `fault current limiters".

F.	The rating and characteristics of fault current limiters shall be such as to limit the fault current of the ultimate circuit breaker in the circuit to the fault current capacity of the circuit breaker. Fault current limiters shall be such that they will not operate under overload as distinct from short circuit conditions. Fault current limiters shall be labelled as such.

G.	Equipment fixed inside cubicles shall be required to give easy access to wiring and terminals. Resistance boxes shall be located so that the adjustment screws are on a vertical accessible face. Stud terminals shall be provided for all resistances.

2.06	TERMINAL BOARDS

A.	Grouped terminal boards of adequate capacity and fully numbered, with permanent labels, shall be provided for all wires leading to equipment outside a panel. Terminal numbers or markings shall correspond with those used on related apparatus and wiring diagrams. Removable plates or  other facility shall be provided for the entry of incoming cables, conduits, trunking, etc. with means for effective earthing to the cubicle chassis. Provision shall be made for the earthing of all non current-carrying metalwork. For main power terminals incorporated within a panel, soldered socket type terminals shall be provided.

B.	All terminal boards shall be mounted in accessible positions and when in enclosed cubicles, are preferably to be inclined towards the doors. Spacing of adjacent terminal boards shall be not less than 100 mm and the bottom of each board shall be not less than 200 mm above the incoming cable gland plate. Separate terminations shall be provided on each terminal strip for the cores of incoming and outgoing cables including all spare cores. Barriers shall be provided between wires of different voltages on the same or adjacent terminals.

C.	Terminals that are "live" from other power sources when the cubicle isolator is open shall be shrouded and fitted with a danger label.

D.	Screw or stud type terminals shall only be used with crimped ring type wiring terminations. Plain steel screws and studs shall be not less than size M6 but stainless steel and bronze down to size M5 may be used provided that the current carrying capacity is adequate. All studs shall be provided with nuts, washers and lock washers.

E.	Insertion type terminals shall generally be employed for small circuit wiring whereby the stranded conductor or crimped termination is clamped between plates by a screw having a suitable locking device. Terminal entries shall be shrouded such that no current carrying metal is exposed. Tapped holes shall have not less than three full threads.

F.	Terminal assemblies are preferably to be of the unit form suitable for mounting collectively on a standard assembly rail, secured from the front and giving the required number of ways plus 10% spare.

G.	All connections shall be made at the front of the terminal boards and no live metal is to be exposed at the back.

H.	No more than two leads shall be taken to any common pair of terminals, unless specially approved by the Engineer.

2.07	NUMBER PLATES AND LABELS

A.	Number plates and labels shall be provided and fixed to all items, including push buttons, operating levers, indicating lamps, etc. to show the purpose and function of each item and to ensure its safe and satisfactory operation. The type, size, inscription and position of labels shall be to the Engineer's approval.

B.	Adhesive die stamped or printed tapes shall not be permitted for labelling equipment.

2.08	EARTHING

A.	All control panels shall be provided with a continuous copper earth bar having a sectional area of not less than 75 mm2 placed at a convenient position near the bottom of the panel. The area of the earth bar shall not be less than half the cross-sectional area of the phase busbars and not less than the area of the incoming neutral conductor.

B.	All metal cases or earth terminals of the various instruments, relays, etc. on the panels shall be connected to this earth bar by copper connections of not less than 2.5 mm2.

C.	All metal parts other than those forming part of any electrical circuit shall be earthed in an approved manner and all earthing terminals shall be of adequate dimensions.

2.09	ANTI CONDENSATION HEATERS

A.	Where ever required, anti-condensation heaters shall be provided in control panels, switchboards and motors to prevent internal condensation due to atmospheric or load variations. The heaters shall be thermostatically controlled and of sufficient capacity to maintain 5oC temperature differential with the surrounding atmosphere. The heater circuit shall include an isolating switch and indicator lamp to show "Heater Circuit On". The heaters may be energized from a 220V, 50Hz supply, as applicable.

B.	When maintaining equipment fitted with heaters it will be necessary to switch off both the main isolating switch and the switch for the heater. A warning notice of this danger shall be fitted near the terminal box of every remote heater and at every panel fitted with heaters.

C.	All equipment fitted with heaters shall be such that the maximum permitted rise in temperature is not exceeded if the heaters are energized while the equipment is in operation and as such must be provided with suitable ventilation.

D.	All such equipment, whether fitted with a heater device or not, shall be provided with suitable drainage and be free from pockets in which moisture can collect.

2.10	MOTOR STARTERS

A.	Motor starter enclosures shall be at least to the standards specified for LV switchgear.

B.	Motor starters shall be of the following types and suitably rated for each application:-

MANUAL 		= UNDER 0.34 KW MOTORS

DIRECT ON LINE 	= UP TO 5 KW MOTORS

STAR DELTA		= ABOVE 5 KW MOTORS

AUTO TRANSFORMER WHEN SUPPLIED BY THE MOTOR MANUFACTURER.

C.	Auto-transformer type motor starters when supplied shall each comprise:

1.	Triple pole mechanically interlocked isolator with padlocking facilities in the 'off' position.

2.	H.R.C fuses in the power circuit.

3.	Adequately rated autotransformer.

4.	Contractors rated at 15 starts per hour suitable for pushbutton operation, with magnetic blowouts and arc chutes on each pole, hard drawn copper main contacts of the removable type, and continuously rated operating coils.

5.	Under voltage release.

6.	Overload relays of the adjustable electro-magnetic type with oil dashpot time lags and reset facilities, calibrating plates shall be scaled in amperes or equivalent thermal compensated type.

7.	Control circuit fuses of the cartridge type.

8.	Single phase preventative device.

9.	Ammeter of the moving iron type.

10.	Pilot lamp to indicate "motor-running".

11.	Removable neutral link of heavy section copper.

D.	The Star/Delta motor starters shall each comprise:

1.	Triple pole mechanically interlocked isolator with padlocking facilities in the "off" position.

2.	H.R.C. fuses in the power circuit.

3.	Contractors rated at 15 start per hour suitable for pushbutton operation, with magnetic blowouts and arc chutes on each pole, hard drawn copper main contacts of the removable type and continuously rated operating coils.

4.	Under voltage release.

5.	Overload relay of the adjustable thermal type.

6.	Control circuit fuses of the cartridge type.

7.	Motor protection relay (unbalance and single phasing)

8.	Ammeter of the moving iron type.

9.	Pilot lamp to indicate "motor running".

10.	Removable neutral link of heavy section copper.

E.	Direct-on-line type motor starters shall each comprise:

1.	Triple pole mechanically interlocked isolator with padlocking facilities in the "off" position.

2.	H.R.C. fuses in the power circuit.

3.	Contractor rated at 15 starts per hour suitable for pushbutton operation, with magnetic blowouts and arc chutes on each pole, hard drawn copper main contacts of the removable type, and continuously rated operating coils.

4.	Under voltage release.

5.	Overload relays of the adjustable thermal type.

6.	Control circuit fuses of the cartridge type.

7.	Motor protection relay (unbalance and single phasing).

8.	Ammeter of the moving iron type for motors in excess of 5 Kw.

9.	Pilot lamp to indicate "motor running".

10.	Removable neutral link of heavy section copper.

F.	For starters incorporating reduced voltage starting the change over shall be automatic. A lock-off switch shall be provided and located locally to each motor and connected into the starter control circuit so that the starter cannot be operated when the switch is in the "off" position.

G.	"Hand/off/Auto" switches shall be provided for all starters.

2.11	ELECTRIC MOTORS

A.	Motors shall be of the totally enclosed fan cooled (TEFC) design to BS 5000 and shall be fitted with axially locating type bearings and/or heavy duty thrust bearings at the non-driving end and roller type bearings at the drive end. All bearings shall be of adequate proportions and design suitable for the particular application.

B.	Motors shall be of the squirrel cage induction type. Motors shall be suitably finished to afford protection against any corrosive liquid or fumes.

C.	All motors shall be built of high-grade components and materials and shall operate without undue vibration and with the minimum of noise.

D.	The insulation shall be Class `F' to BS 2757 but the temperature rise shall be limited to 80 oC measured by the resistance method, at an ambient temperature of 50 oC. The motors shall be suitable in all respects for their operational duties taking into account such an ambient temperature within the building.

E.	All motors rated at 11 KW and above shall be fitted with thermostatic control elements actuating directly on the control circuit of the motor and disconnecting it from the supply in the event of a temperature rise exceeding the acceptable limits for its insulation class.

F.	The motors shall be fully tropicalised, and shall be fitted with anti-condensation heaters.

G.	The motors shall be capable of providing 10% in excess of the specified volume flow of their respective fans under all operating conditions. Selections must assume that resistance increases by the square law and absorbed power by the cube law.

H.	Motors are required to operate from a 380V, 3 phase or 220V single phase, 50Hz supply as applicable, and shall be continuously rated.

J.	The motors shall be capable of satisfactory operation with a voltage variation of 10% above or below the supply voltage. They shall also be capable of operating satisfactorily with a frequency variation of 2.5% above or below the normal frequency of 50 Hz, as applicable.

1.	No motor shall run faster than 1500 RPM unless otherwise approved by the Engineer or indicated on drawings.

2.	Motors shall be designed to operate at a power factor not less than 0.85.

3.	Motors shall be suitable for the starting methods specified.

4.	Motor starting currents shall not exceed the following values:-

Autotransformer starting - 1.5 times the full load current.

Star/Delta starting - 3.5 times the full load current.

Direct-on-line starting - 6 times the full load current.

K.	The connections of the motors shall be brought out to easily accessible terminals of the stud type, totally enclosed. They shall be substantially designed and thoroughly insulated from the frame. Cambric or equal insulation shall be used for the connections from the windings to the terminals. Terminal boxes shall be fitted with glands to accept the specified type of cable.

L.	The cable glands shall be downward pointing at such an angle as is necessary to clear the motor base plate and plinth.

M.	Motors shall have visible nameplates indicating:-

Motor power	--- KW

Voltage

Phase

Cycles

RPM

Full load amps,

Locked Rotar amps

Frame size

Manufacturers name and model

Power factor

# PART 3 EXECUTION

3.01	INSTALLATION

A.	Installation of all the equipment, plant and material included in this Section of the Specification shall additionally be in accordance with the requirements of  Electrical Specificationsز

END OF SECTION 15171

| DIVISION – 15 MECHANICAL # SECTION – 15185 | TECHNICAL SPECIFICATION MECHANICAL WORK HYDRONIC PUMPS |
| --- | --- |

PART 1 - GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following:

      - Separately coupled, horizontal, in-line centrifugal pumps.

      - Separately coupled, vertical, in-line centrifugal pumps.

      - Separately coupled, base-mounted, end-suction centrifugal pumps.

      - Horizontal split case centrifugal pump.

      - Variable speed pumping system for hot water pumps.

      - Pump specialty fittings.

  - DEFINITIONS

    - Buna-N:  Nitrile rubber.

    - EPT: Ethylene propylene terpolymer.

  - SUBMITTALS

    - Product Data: Include certified performance curves and rated capacities, operating characteristics, furnished specialties, final impeller dimensions, and accessories for each type of product indicated. Indicate pump's operating point on curves.

    - Shop Drawings: Show pump layout and connections.  Include setting drawings with templates for installing foundation and anchor bolts and other anchorages.

      - Wiring Diagrams:  Power, signal, and control wiring.

    - Operation and Maintenance Data:  For pumps to include in emergency, operation, and maintenance manuals.

  - QUALITY ASSURANCE

    - Source Limitations: Obtain hydronic pumps through one source from a single manufacturer.

    - Product Options: Drawings indicate size, profiles, and dimensional requirements of hydronic pumps and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

    - Electrical Components, Devices, and Accessories: Listed  and  labeled  as  defined  in  NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

  - WARRANTY

Provide 12 months warranty from the date of taking over certificate in accordance with contract conditions

.

  - DELIVERY, STORAGE, AND HANDLING

    - Manufacturer's Preparation for Shipping: Clean flanges and exposed machined metal surfaces and treat  with anticorrosion compound after assembly and testing. Protect flanges, pipe openings, and nozzles with wooden flange covers or with screwed-in plugs.

    - Store pumps in dry location.

    - Retain protective covers for flanges and protective coatings during storage.

    - Protect bearings and couplings against damage from sand, grit, and other foreign matter.

    - Comply with pump manufacturer's written rigging instructions.

  - COORDINATION

    - Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

  - EXTRA MATERIALS

    - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

      - Mechanical Seals: One mechanical seal(s) for each pump.

PART 2 - PRODUCTS

  - SEPARATELY COUPLED, HORIZONTAL, IN-LINE CENTRIFUGAL PUMPS

    - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in- line pump; designed for installation with pump and motor shafts mounted horizontally. Rate pump for 175-psig (1204-kPa) minimum working pressure and a continuous water temperature of 225 deg F (107 deg C).

    - Pump Construction:

      - Casing:  Radially split, cast iron, with threaded gage tappings at inlet and outlet, and threaded

companion-flange connections.

      - Impeller:  cast bronze; statically and dynamically balanced, and keyed to shaft.  Trim impeller to match specified performance.

      - Pump Shaft:  Stainless steel.

      - Mechanical Seal:  Carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Buna-N bellows and gasket. Include water slinger on shaft between motor and seal.

      - Pump Bearings:  Permanently lubricated ball bearings.

    - Shaft Coupling: Molded rubber insert with interlocking spider capable of absorbing vibration.

    - Motor: Single speed, with permanently lubricated ball bearings, unless otherwise indicated; and rigidly mounted to pump casing. Comply with requirements in Division 15 Section "Motors."

  - SEPARATELY COUPLED, VERTICAL, IN-LINE CENTRIFUGAL PUMPS

    - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in- line pump; designed for installation with pump and motor shafts mounted vertically. Rate pump for 175-psig (1204-kPa) minimum working pressure and a continuous water temperature of 225 deg F (107 deg C).

    - Pump Construction:

      - Casing:  Radially split, cast iron, with replaceable bronze wear rings, threaded gage tappings

at inlet and outlet, and threaded companion-flange connections.

      - Impeller:  cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a locking cap screw. Trim impeller to match specified performance.

      - Pump Shaft:  Stainless steel.

      - Mechanical Seal:  Carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Buna-N bellows and gasket. Include water slinger on shaft between motor and seal.

      - Packing Seal: Stuffing box, with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

      - Pump Bearings:  Permanently lubricated ball bearings.

    - Shaft Coupling:  Axially split spacer coupling.

    - Motor:  Single speed, with permanently lubricated ball bearings, unless otherwise indicated; rigidly mounted to pump casing with lifting eye and supporting lugs in motor enclosure. Comply with requirements in Division 15 Section "Motors."

  - SEPARATELY COUPLED, BASE-MOUNTED, END-SUCTION CENTRIFUGAL PUMPS

    - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, end- suction  pump; designed for base mounting, with pump and motor shafts horizontal. Rate pump for 175-psig (1204-kPa) minimum working pressure and a continuous water temperature of 225 deg F (107 deg C).

    - Pump Construction:

      - Casing: Radially split, cast iron, with replaceable bronze wear rings, threaded gage tappings at inlet and outlet, drain plug at bottom and air vent at top of volute, and flanged connections. Provide integral mount on volute to support the casing, and attached piping to allow removal and replacement of impeller without disconnecting piping or requiring the realignment of pump and motor shaft.

      - Impeller: cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a locking cap screw. Trim impeller to match specified performance.

      - Pump Shaft:  Stainless steel.

      - Mechanical Seal: Carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Buna-N bellows and gasket.

      - Packing Seal: Stuffing box, with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

      - Pump Bearings: Grease-lubricated ball bearings contained in cast-iron housing with grease

fittings.

    - Shaft Coupling: Molded rubber insert and interlocking spider capable of absorbing vibration.  EPDM coupling sleeve for variable-speed applications.

    - Coupling Guard: Dual rated; steel; removable; attached to mounting frame.

    - Mounting Frame: Welded-steel frame and cross members, factory fabricated from channels and angles.  Fabricate to mount pump casing, coupling guard, and motor.

    - Motor: Single speed, with permanently lubricated ball bearings, unless otherwise indicated; secured to  mounting frame, with adjustable alignment. Comply with requirements in Division 15 Section "Motors."

  - HORIZONTAL SPLIT CASE CENTRIFUGAL PUMP (HSC)

    - Description: horizontal, base mounted,  horizontally  split  case,  double  suction,  single  stage, centrifugal type, directly connected to motor through heavy duty flexible coupling and with heavy gauge coupling guard.

    - Base: Pump and motor to be mounted on common cast iron base reinforced against deflection, with drip rim, drain tapping, bolt holes, and grouting hole.

    - Pump Casing: Cast Iron, high tensile strength alloy, designed for working pressure of 2000 kPa, fitted with  easily removable bronze wear rings dowelled to casing. Casing to be divided at horizontal centerline and the 2 halves accurately machined, dowel aligned and bolted together.

    - Suction and discharge nozzles to be in-line piping design, cast integrally with lower half of pump casing to allow rotating element to be removed without disconnecting suction and discharge flanges.

    - Impeller: Bronze, enclosed, double suction type, fastened to shaft by stainless-steel key and screw locked adjustable shaft sleeves.

    - Shaft and Shaft Sleeves: Shaft to be high stainless steel, sized to carry axial and radial thrust with minimum deflection and protected against corrosion from water by full length bronze shaft sleeves. Teflon  gaskets to be provided between impeller hub and shaft sleeves to prevent pumped water corroding shaft.

    - Mechanical Seal: Ni-resist face, carbon washer and stainless steel metal parts.

    - Bearings: Pump rotating element to be supported by two heavy duty grease lubricated ball bearings for  both radial and thrust loads, mounted in  machined moisture  proof  and  dustproof  cast  iron housings  bolted to pump casing with register fits to ensure permanent alignment. Bearing housing supports to be cast integrally with lower half of pump casing.

    - Pump shall be installed with inertia base type foundation including steel frame, concrete and spring to the approval of the Engineer.

  - VARIABLE SPEED PUMPING SYSTEM FOR HEATING WATER PUMPS

    - Supply and install wherever shown on drawings centrifugal pumps (as described before) and of types and capacities as shown on drawings and pump schedule.

      - Variable Speed Pumping Package

        - Pumping Skid.

        - Pump Control Panel.

        - Adjustable Frequency Drive.

        - Automatic Bypass.

        - Sensor Transmitters.

        - Sequence of Operation.

      - Submittals

        - Submittals shall include the following:

- System summary sheet.

- Sequence of operation.

- Shop drawing indicating dimensions, required clearances and location and size of each field connection.

- Power and control wiring diagrams.

- System profile analysis including variable speed pump curves and system curve. The analysis shall also include pump, motor and AFD efficiencies, job specific load profile, staging points, horsepower and kilowatt/hour consumption.

- Pump data sheets.

        - Submittals must be specific to this project. Generic submittals will not be accepted.

      - Quality Assurance

        - The pumping package shall be assembled by the pump manufacturer. An assembler of pumping systems not actively engaged in the design and construction of centrifugal pumps shall not be considered a pump manufacturer. The manufacturer shall assume “Unit Responsibility” for the complete pumping package. Unit responsibility shall be defined as responsibility for interface and successful operation of all system components supplied by the pumping system manufacturer.

        - The  manufacturer  shall  have  a  minimum  of 20  years’ experience  in  the  design  and construction of variable speed pumping systems.

        - All functions of the variable speed pump control system shall be tested at the factory prior to shipment. This test shall be conducted with motors connected to AFD output and it shall test all inputs, outputs and program execution specific to this application.

        - The manufacturer shall be fully certified by the International Standards Organization per ISO 9007. Proof of this certification shall be furnished at time of submittal.

        - Manufacturer shall be listed by Underwriter’s Laboratories as a manufacturer of packaged pumping systems.

        - Bidders shall comply with all sections of this specification relating to packaged pumping systems. Any deviations from this specification shall be bid as a voluntary alternate clearly defined in writing. If no exceptions are noted, the supplier or contractor shall be bound by these specifications.

      - Manufactured Units

        - Furnish and install as shown on the plans a Variable Speed Pumping System.

        - The control system shall include, as a minimum, pump & motor assemblies, the programmable logic pump controller, adjustable frequency drive(s), automatic bypass, suction and discharge piping and additional equipment as specified or as required to properly execute the sequence of operation. Furnish field installed remote sensor/transmitters as indicated on the plans.

        - System shall require only suction and discharge connections and a single point power

connection. Field connection of remote sensor/transmitters and connection to Building Automation System shall be by controls contractor.

        - All components shall be mounted on a structural steel base suitable for grouting. The base shall be large enough to support the system's pumps, piping and control panel. All welded pressure bearing piping must be fabricated with full penetration welds.

        - Provide pumps as indicated on the pump schedule. Pumps and motors shall be furnished as specified in respective sections of this document.

        - Pressure gauges shall be furnished for system supply and return headers. Gauges shall be installed to be clearly visible from front of control panel.

        - Variable speed motors shall be inverter-duty motor and shall comply to NEMA MGI part

        - Variable speed drives shall be with automatic by pass for fixed speed operation incase

the VFD is not operating.

      - Components

        - Pump Logic Controller.

          - The Technologic pump logic controller assembly shall be listed by and bear the label of Underwriter's Laboratory, Inc. (UL). The controller shall meet Part 15 of FCC regulations pertaining to class A computing devices. The controller shall be specifically designed for variable speed pumping applications.

          - The controller shall function to a proven program that safeguards against damaging hydraulic conditions including:

            - Motor overload

            - Pump flow surges

            - Hunting

            - End of curve

          - The pump logic controller shall be capable of accepting 8 analog inputs from zone sensor/transmitters indicated at various position of the piping network and as approved by the Engineer. The controller shall scan each analog input a minimum of once every 500 milliseconds. It will then select the analog signal that has deviated the greatest amount from its setpoint. This selected signal will be used as the command feedback input for a hydraulic stabilization function to minimize hunting. Each input signal shall be capable of maintaining a different set point value.

          - The pump controller shall be capable of controlling all pumps in parallel.

          - The controller shall be field expandable to control up to 2 pumps in parallel and accept up 16 analog inputs. This modification shall consist of nothing more than the addition of analog input modules and shall not require the use of special tools or factory reprogramming. Controllers not capable of being expanded to this level will not be acceptable.

          - The hydraulic stabilization program shall utilize a proportional-integral-derivative control function. The proportional, integral and derivative values shall be user adjustable over an infinite range.

          - The pump logic controller shall be self prompting. All messages shall be displayed in plain English. The operator interface shall have the following features:

            - Multi-fault memory and recall.

            - On-screen help functions.

            - LED pilot lights and switches.

            - Soft-touch membrane keypad switches.

          - The readout  shall  be two  lines of  forty 0.50"  brightly lit  fluorescent  characters

capable of displaying the following values:

            - Differential pressure in PSIG.

            - Pressure in PSIG.

            - Flow in GPM.

            - Temperature in degrees F or C.

            - Differential temperature in degrees F or C.

            - BTU calculation.

            - Kilowatt consumption.

            - Tons per hour calculation.

            - Wire to water efficiency calculation.

          - The following communication features shall be provided to the BAS:

            - Remote system start / stop.

            - Failure of any system component.

            - Process variable.

            - AFD speed.

        - Adjustable Frequency Drive:

          - The adjustable frequency drive(s) shall be pulse width modulation (PWM) type, microprocessor controlled design.

          - The AFD, including all factory installed options, shall have CSA approval.

          - Enclosure shall be NEMA 1 ventilated for installation as a wall mounted or free- standing unit, depending on the amp rating. A hand-off automatic switch and speed potentiometer shall be mounted on the front of the enclosure.

          - AFD shall utilize a diode bridge rectifier to convert three phase AC to a fixed DC voltage. Power factor shall remain above 0.95 regardless of speed or load. AFDs employing power factor correction capacitors shall not be acceptable.

          - Insulated gate bipolar transistors shall be used in the inverter section to convert the fixed DC voltage to a three phase, adjustable frequency, AC output. A DC line reactor shall be provided to minimize harmonic and current distortion of the input power line.

          - The following customer modifiable adjustments shall be provided:

            - Accel time: 0.1 to 1800 seconds.

            - Decel time: 0.1 to 1800 seconds.

            - Minimum frequency: 0 HZ.

            - Analog input filter: 0.1 to 10 seconds.

            - Analog outputs: 10 to 1 gain.

            - Volts / Hertz ratio.

          - Speed reference signal shall be customer selectable for 0-10 VDC or 4-20 mA.

          - The AFD shall be suitable for elevations to 3300 feet above sea level without derating. Maximum operating ambient temperature shall not be less than 104 degrees

F. AFD shall be suitable for operation in environments up to 95% non-condensing humidity.

          - The AFD shall be capable of displaying the following information in plain English via a 40 character alphanumeric display:

            - Frequency

            - Voltage

            - Current

            - Kilowatts per hour

            - Fault identification

            - Percent torque

            - Percent power

            - RPM

          - All AFDs shall be warranted for a period of 12 months after shipment. This warranty shall cover parts and labor. Variable speed drives shall be with manual bypass for fixed speed operation in case the VFD is not operating. Starter in manual bypass to be Star Delta type.

        - Automatic AFD Bypass:

          - Variable speed pumping system shall be equipped with an automatic bypass.

          - Bypass shall consist of a main power disconnect with ground fault protection, a pair

of interlocked contactors and a motor overload relay to have Star Delta starter. All are to be mounted in a NEMA 1 enclosure.

          - Automatic bypass shall operate as described in the sequence of operation.

        - Sensor / Transmitters

Provide the required number of field mounted differential pressure sensor transmitter(s) as indicated on the plans. Unit shall transmit an isolated 4-20mA dc signal indicative of process variable to the pump logic controller via standard two wire 24 DC system. Unit shall have stainless steel wetted parts with two 0.25" male NPT process connections. It shall be protected against radio frequency interference and shall have a watertight, NEMA 4 electrical enclosure capable of withstanding 2000 PSI static pressure with a 0.5" NPT conduit connection. Accuracy shall be within 0.25% of full span.

        - Sequence of Operation

          - The system shall consist of a Technologic pump logic controller, multiple pump/AFD sets with manual and automatic alternation and pump starting with across the line bypasses for each pump.

          - The pumping system shall start upon the closure of customer's contact when the pump logic controller Mode of Operation selector switch is in the REMOTE position.

          - When the pump logic controller selector switch is in the LOCAL position, the pumping system shall operate automatically.

          - Sensor/transmitters shall be provided as indicated on the plans.

          - Each sensor/transmitter shall send a 4-20mA signal to the pump logic controller, indicative of process variable condition.

          - The   pump   logic   controller   shall   compare   each   signal   to   the   independent,

engineer/user determined set points.

          - When all set points are satisfied by the process variable, the pump speed shall remain constant at the optimum energy consumption level.

          - When all set points are satisfied by the process variable, the pump speed shall remain constant at the optimum energy consumption level.

          - The Technological pump logic controller shall continuously scan and compare each process variable to its individual set point and control to the least satisfied zone.

          - If the set point cannot be satisfied by the designated lead pump, the pump logic controller shall initiate a timed sequence of events to stage a lag pump.

          - The lag pump shall accelerate resulting in the lead pump(s) decelerating until they equalize in speed.

          - Further change in process variable shall cause the pumps to change speed together.

          - When the set point criteria can be safely satisfied with fewer pumps, the Technologic pump logic controller shall initiate a timed destage sequence and continue variable speed operation.

          - As the worst case zone deviates from set point, the pump logic controller shall send the appropriate analog signal to the AFD to speed up or slow down the pump/motor.

          - The operation of the pumps in the failure mode shall be started through the pump logic controller and an across the line bypass.

          - When in the "AUTOMATIC" mode, the pump(s) shall operate through the AFD(s) being controlled by a signal generated by the pump logic controller.

          - In the event of a system differential pressure failure, due to a pump, AFD, overload fault, the pump logic controller shall automatically initiate a timed sequence of events to start the remaining pump/AFD set(s) in the variable speed mode.  A message on the display shall indicate the fault, pump/motor, or AFD. Subsequent failures shall initiate a timed sequence of events to the variable speed mode as available.

          - In the event of all AFD faults, all pumps shall be automatically started across the line.

          - When in the "BYPASS" mode, the selected pump(s) shall be able to be operated across the line at constant speed with motor overload protection. A solid red light shall signal this condition. All pumps shall be locked out of the variable speed mode.

          - In the event of the failure of a zone sensor/transmitter, its process variable signal shall     be  removed  from  the  scan/compare   program.   Alternative   zone sensor/transmitters, if  available,  shall  remain  in  the  scan/compare  program  for control.

          - The zone number corresponding to the failed sensor/transmitter shall be displayed on the operation interface of the pump logic controller. In the event of failure of any pump or its AFD, the standby pump shall operate automatically. A message on the display shall indicate the fault, pump/motor or AFD with remote signal to BMS.

          - In the event of failure to receive all zone process variable signals, the AFD shall maintain 100% speed, reset shall be automatic upon correction of the zone failure.

          - PUMP, AFD, OVERLOAD fault shall be continuously scrolled through the display on the operator interface of pump logic controller until the fault has bee corrected and the controller has been manually reset.

  - PUMP SPECIALTY FITTINGS

    - Suction Diffuser: Angle pattern, 175-psig (1204-kPa) pressure rating, cast iron body and end cap, pump-inlet fitting; with bronze startup and bronze or stainless-steel permanent strainers; bronze or stainless-steel straightening vanes; drain plug; and factory-fabricated support.

    - Triple-Duty Valve: Angle or straight pattern, 175-psig (1204-kPa) pressure rating, cast iron body, pump-discharge  fitting;  with  drain  plug  and  bronze-fitted  shutoff,  balancing,  and  check  valve features. Brass gage ports with integral check valve, and orifice for flow measurement.

PART 3 - EXECUTION

  - EXAMINATION

    - Examine equipment foundations and anchor-bolt locations for compliance with requirements for installation tolerances and other conditions affecting performance of work.

    - Examine roughing-in for piping systems to verify actual locations of piping connections before pump installation.

    - Examine foundations and inertia bases for suitable conditions where pumps are to be installed.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - PUMP INSTALLATION

    - Install pumps with  access  for  periodic  maintenance  including  removal  of  motors,  impellers, couplings, and accessories.

    - Independently support pumps and piping so weight of piping is not supported by pumps and weight of pumps is not supported by piping.

    - Set base-mounted pumps on  concrete foundation.  Disconnect coupling before setting.   Do not reconnect couplings until alignment procedure is complete.

      - Support pump baseplate on rectangular metal blocks and shims, or on metal wedges with small taper, at points near foundation bolts to provide a gap of 3/4 to 1-1/2 inches (19 to 38 mm) between pump base and foundation for grouting.

      - Adjust metal supports or wedges until pump and driver shafts are level. Check coupling faces

and suction and discharge flanges of pump to verify that they are level and plumb.

  - ALIGNMENT

    - Align pump and motor shafts and piping connections after setting on foundation, grout has been set and foundation bolts have been tightened, and piping connections have been made.

    - Comply with pump and coupling manufacturers' written instructions.

    - After alignment  is  correct,  tighten  foundation  bolts  evenly but  not  too  firmly.  Completely  fill baseplate with nonshrink, nonmetallic grout while metal blocks and shims or wedges are in place. After grout has cured, fully tighten foundation bolts.

  - CONNECTIONS

    - Piping installation requirements are specified in  other Division 15 Sections.	Drawings indicate general arrangement of piping, fittings, and specialties.

    - Install piping adjacent to machine to allow service and maintenance.

    - Connect piping to pumps.  Install valves that are same size as piping connected to pumps.

    - Install check valve and throttling / triple-duty valve on discharge side of pumps.

    - Install suction diffuser and shutoff valve on suction side of pumps.

    - Install flexible connectors on suction and discharge sides of base-mounted pumps between pump casing and valves.

    - Install pressure gages on pump suction and discharge, at integral pressure-gage tapping, or install single gage with multiple input selector valve.

    - Install electrical connections for power, controls, and devices.

  - STARTUP SERVICE

    - Engage a factory-authorized service representative to perform startup service.

      - Complete installation and startup checks according to manufacturer's written instructions.

      - Check piping connections for tightness.

      - Clean strainers on suction piping.

      - Perform the following startup checks for each pump before starting:

        - Verify bearing lubrication.

        - Verify that pump is free to rotate by hand and that pump for handling hot liquid is free to rotate with pump hot and cold. If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

        - Verify that pump is rotating in the correct direction.

      - Prime pump by opening suction valves and closing drains, and prepare pump for operation.

      - Start motor.

      - Open discharge valve slowly.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain hydronic pumps.

END OF SECTION 15185

| DIVISION – 15 MECHANICAL SECTION – 15190 | TECHNICAL SPECIFICATION MECHANICAL WORK MECHANICAL IDENTIFICATION |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This Technical Specification establishes the type and quality of materials and the standard of workmanship to be used in the supply and installation of Mechanical Identification systems.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and installation of Mechanical Identification systems as specified herein and where referred to on the Drawings.

B.	Coordination:  The Contractor shall be responsible for the full coordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	Manufacturers:  Firms regularly engaged in the manufacture of Mechanical Identification systems whose products have been in satisfactory use for a similar application and not less than 10 years.

B.	Installer:  Firms regularly engaged and qualified in the installation of Mechanical Identification systems with at least 5 years successful installation experiences on projects of a similar nature.

1.04	APPLICABLE CODES AND STANDARDS

A.	Mechanical Identification systems and all associated materials and workmanship shall comply fully with the latest relevant British Standards in all respects.

The following are the most commonly used and relevant British Standards associated with pipe work products and associated materials.  However, the Contractor shall ensure that all applicable British Standards are complied with whether listed here or not.

BS 1710	-	Specification for Identification of Pipelines and Services.

BS 4800	-	Specification for Paint Colours for Building Purposes.

1.05	SUBMITTALS

A.	Drawings refer to 15010

B.	Products: Full manufacturers colour data for each product.

C.	Samples - Full - size colour sample of pipe work and ductwork identification.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with 15010

B.	Mechanical identification system shall correspond totally to "As Built" data.

1.07	WARRANTY

A.	Provide 12 months warranty in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	PLANT AND PIPEWORK IDENTIFICATION

A.	All pipe work shall be colour coded in accordance with BS 1710 as detailed in Table 1.

TABLE I

IDENTIFICATION OF PIPELINES

_______________________________________________________________

Pipe contents				Colour code		Basic

indication	 	colour

(approx			(approx

100mm)		150mm)

________________________________________________________________

Drinking Water			To BS 1710			Blue

Cold water down service		To BS 1710   		Green

Drainage				To BS 1710			Black

LPG	                                      	To BS 1710			Yellow

________________________________________________________________

B.	Identification to pipe work shall consist of 100mm PVC adhesive bands over the basic colour and shall include flow direction arrows together with the abbreviation of the service name.  All coding requirements are to be agreed with the Engineer.

C.	Code indication for safety conditions shall be as follows:-

Safety Colour			    BS colour reference

BS 4800

Red					04  E  53

Yellow					08  E  51

Auxiliary Blue				18  E  53

Safety colour references are as follows: -

1.	Red for fighting equipment.

2.	Yellow with black diagonal stripes for warning of danger.

3.	Yellow with trefoil symbol for ironizing radiation

(as defined in BS 3510).

4.	Auxiliary blue in connection with green basic colours, to denote pipes carrying fresh water, either potable or non-potable.

Safety colour references shall be applied using 100mm wide sections of PVC adhesive band in all permanent locations, to be agreed with the Engineer.

Colour references shall include notation as follows:-

1.	FIRE

2.	DANGER

3.	RADIATION

4.	POTABLE OR NON-POTABLE

In the case of fire service, all equipment, i.e. valves, suction tanks, etc., shall also be painted red.

D.	Un insulated pipe work shall be painted with one coat of undercoat and two coats of gloss finish to the relevant BS colour.

E.	Valve identification shall be by means of 40mm diameter traffalyte discs of white/black/white composition.  Letters and figures of 8mm minimum height, identifying the service and valve number shall be engraved into the material.  A 3mm diameter hole shall be drilled through the disc for the purpose of securing the disc to the valve.

F.	Plant identification shall be by means of traffalyte labels of white/black/white composition.  Letters and figures of 8mm minimum height identifying the plant shall be of a size to be agreed with the Engineer.  A minimum of two 3mm diameter holes shall be drilled through the label to the plant.

G.	All plants shall carry the manufacturer's identification plate which shall incorporate all details of electrical and mechanical duties.

2.02	DUCTWORK IDENTIFICATION

A.	Ductwork shall be colour coded in accordance with HVAC Specification DW142 to the colours indicated in Table 2.  For conditioned air, identification shall comprise either of two symbols (one red, one blue)  or a single symbol coloured, part red, part blue.

TABLE  2

DUCT IDENTIFICATION COLOURS

| Type | Colour | BS 4800 |
| --- | --- | --- |
| Conditioned Air Warm Air Fresh Air Exhaust / extract recirculated air Foul Air | Red and Blue Yellow Green Grey Brown | 04353 / 18E53 10E53 14E53 AA009 06C39 |

B.	Direction of flow shall be by PVC self adhesive equilateral triangles with one apex pointing in the direction of flow.  The minimum length of side of the triangle shall be 150mm.

# PART 3 EXECUTION

3.01	STORAGE

A.	All identification materials shall be stored within a well lit container or purpose made compartmented racks or shelving.  The material shall be adequately covered to prevent damage and ingress of dirt.

3.02	GENERAL

A.	Identification shall be placed where it can be easily seen and at positions where identification will be required.  To ensure that the symbols are seen, the following points shall be considered:-

1.	The symbols shall be on the surface which faces the positions of normal access to the completed installation.

2.	The symbols shall not be hidden from view by structural members, other ducts, plant or other services distribution systems.

3.	The symbols shall be placed where there is adequate natural or artificial light.

B.	Symbols shall occur frequently enough to avoid the need for ducts and pipes to be traced back.  Symbols should be placed at any service and access points to the distribution system.

C.	Identification shall be applied to pipe work and ductwork at every entry and exit point to a room but in no case of intervals of less than 12m.

3.03	PLANT AND PIPEWORK IDENTIFICATION

A.	In addition to the colour bands, all pipe work in plant rooms and service areas, whether insulated or not, shall be legibly marked with black or white letters to indicate the type of service and the direction of flow.  Services shall be identified as follows:-

Refrigerant:				RFG

Cold Water:		Raw 		RW

Sweet 	SW

Domestic Hot Water:Raw 	           RW

Sweet 	SW

Fire Main:				FM

Gas: 					GAS

B.	The basic identification colour shall be applied using PVC adhesive band either applied to pipe work insulation or pipe when un-insulated. Identification shall be placed at all junctions, at both sides of valves, services appliances, bulkheads, wall penetrations and at any other places where identification is necessary or advantageous.

C.	Where pipes are run in pairs, the letters F and R shall be added to indicate flow and return respectively.

3.04	DUCTWORK IDENTIFICATION

A.	All ductwork in plant rooms and services areas, whether insulated or not, shall be legibly marked with black or white letters to indicated the type of service and the direction of flow.  Services shall be identified as follows:-

Supply Air    	-   	S

Return Air    	-	R

Fresh Air     	-	F

Exhaust  	-	E

B.	Ductwork identification shall be applied to ductwork whether insulated or not, at all branches, plant connections, wall penetrations and at any other place where identification is necessary or advantageous.

END OF SECTION 15190

| DIVISION – 15 MECHANICAL SECTION – 15195 | TECHNICAL SPECIFICATION MECHANICAL WORK LPG GAS PIPING |
| --- | --- |

- PART 1 GENERAL

  - SUMMARY

Section Includes:

LPG gas piping buried beyond 5 feet (1500 mm) of building.

LPG gas piping buried within 5 feet (1500 mm) of building.

LPG gas piping above grade.

Flanges, unions, and couplings.

Pipe hangers and supports.

Valves.

Strainers.

LPG Gas pressure regulators.

Gas pressure relief valves.

Underground pipe markers.

Bedding and cover materials.

  - REFERENCES

    - American Society of Mechanical Engineers:

      - ASME B16.3 - Malleable Iron Threaded Fittings.

      - ASME B31.9 - Building Services Piping.

      - ASME Section IX - Boiler and Pressure Vessel Code - Welding and Brazing Qualifications.

    - American Society for Testing and Materials:

      - ASTM A53 - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

      - ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service.

      - ASTM F708 - Standard Practice for Design and Installation of Rigid Pipe Hangers.

    - American Welding Society:

      - AWS D1.1 - Structural Welding Code - Steel.

    - Manufacturers Standardization Society of the Valve and Fittings Industry:

      - MSS SP 58 - Pipe Hangers and Supports - Materials, Design and Manufacturer.

      - MSS SP 67 - Butterfly Valves.

      - MSS SP 69 - Pipe Hangers and Supports - Selection and Application.

      - MSS SP 78 - Cast Iron Plug Valves, Flanged and Threaded Ends.

      - MSS SP 89 - Pipe Hangers and Supports - Fabrication and Installation Practices.

      - MSS SP 110 - Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends.

    - National Fire Protection Association:

      - NFPA 54 - National Fuel Gas Code.

      - NFPA 58 - Liquefied Petroleum Gas Code.

    - Underwriters Laboratories Inc.:

      - UL 842 - Valves for Flammable Fluids.

  - SYSTEM DESCRIPTION

    - Where more than one piping system material is specified, provide compatible system components and joints. Use non-conducting dielectric connections when joining dissimilar metals in systems.

    - Provide flanges, unions, or couplings at locations requiring servicing. Use unions, flanges, or couplings downstream of valves and at equipment connections. Do not use direct welded or threaded connections to valves, equipment.

    - Provide pipe hangers and supports in accordance with ASME B31.9, and ASTM F708.

    - Use valves for shut-off and to isolate equipment, part of systems, or vertical risers.

  - DEFINITIONS

    - Where the designation LPG is used, it is the abbreviation for Liquefied Petroleum Gas, most commonly Propane.

  - SUBMITTALS

    - Product Data:

      - Piping: Submit data on pipe materials, fittings, and accessories.

      - Valves: Submit manufacturers catalog information with valve data and ratings for each service.

      - Hangers and Supports: Submit manufacturers catalog information including load capacity.

      - Piping Specialties: Submit manufacturers catalog information including capacity, rough-in requirements, and service sizes for the following:

- Strainers.

- Gas pressure regulators.

- Gas pressure relief valves.

    - Design Data: Indicate pipe size. Indicate load carrying capacity of trapeze, multiple pipe, and riser support hangers.

    - Test Reports: Indicate results of piping system pressure test.

    - Welders Certificates: Certify welders employed on the Work, verifying AWS qualification within previous 12 months.

  - CLOSEOUT SUBMITTALS

    - Project Record Documents: Record actual locations of valves, piping system, and system components.

    - Operation and Maintenance Data: Submit for valves and gas pressure regulators installation instructions, spare parts lists.

  - QUALITY ASSURANCE

    - Perform LPG Work in accordance with NFPA 58.

    - Perform Work in accordance with ASME B31.9 code for installation of piping systems and ASME Section IX for welding materials and procedures.

    - Perform Work in accordance with applicable codes.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience.

    - Installer: Company specializing in performing Work of this section with minimum three years documented experience approved by manufacturer.

  - PRE-INSTALLATION MEETINGS

    - Convene minimum one week prior to commencing work of this section.

  - DELIVERY, STORAGE, AND HANDLING

    - Accept valves on site in shipping containers with labeling in place. Inspect for damage.

    - Protect piping and fittings from soil and debris with temporary end caps and closures. Maintain in place until installation. Furnish temporary protective coating on cast iron and steel valves.

  - ENVIRONMENTAL REQUIREMENTS

    - Do not install underground piping when bedding is wet or frozen.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

  - COORDINATION

    - Coordinate trenching, excavating, bedding, backfilling of buried piping systems with other trades.

  - WARRANTY

    - Furnish 12 months manufacturer warranty for valves excluding packing.

  - EXTRA MATERIALS

    - Furnish two packing kits for each type and size valve.

- PRODUCTS

  - LPG GAS PIPING, BURIED AND ABOVE GRADE

    - Copper pipe hard drawn to ASTM B88  K.

      - Fittings: Brazed fittings to ASME B16.

      - Joints: Brazing Welded.

      - Jacket: High quality factory applied sheath with special PVC mixture resistant against external mechanical and chemical attach.

  - PIPE HANGERS AND SUPPORTS

    - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

    - Conform to NFPA 54 and NFPA 58.

    - Hangers for Pipe Sizes 1/2 to 1-1/2 inch (15 to 40 mm): Carbon steel, adjustable swivel, split ring.

    - Hangers for Pipe Sizes 2 inches (50 mm) and Larger: Carbon steel, adjustable, clevis.

    - Multiple or Trapeze Hangers: Steel channels with welded spacers and hanger rods.

    - Wall Support for Pipe 3 inches (80 mm) and Smaller: Cast iron hook.

    - Vertical Support: Steel riser clamp.

    - Floor Support: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.

  - VALVES

    - Ball Valves:

      - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

      - 1/4 inch (6 mm) to 1 inch (25 mm), MSS SP 110, 250 psi (1725 kPa), two piece, threaded ends, bronze body, reinforced teflon seats, blow-out proof stem, lever handle, UL 842 listed for flammable liquids and LPG, full port.

      - 1-1/4 inch (32 mm) to 3 inch (76 mm), MSS SP 110, 250 psi (1725 kPa), two piece, threaded ends, bronze body, reinforced teflon seats, blow-out proof stem, lever handle, UL 842 listed for flammable liquids and LPG, conventional port.

    - Butterfly Valves:

      - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

      - 2 inches (50 mm) and Smaller: MSS SP 67, 175 psi (1200 kPa), bronze body, viton seals, stainless steel trim, lever handle UL listed for gas service, soldered ends, full port.

    - Plug Valves:

      - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

      - 2 inches (50 mm) and Smaller: MSS SP 78, 200 psi (1380 kPa) WOG, threaded ends, round port, full pipe area. Furnish one plug valve wrench for every ten plug-valves with minimum of one wrench.

      - 2-1/2 inches (65 mm) and Larger: MSS SP 78, 200 psi (1200 kPa) WOG, flanged ends, round square port, full pipe area. Furnish wrench-operated.

  - STRAINERS

    - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

    - 2 inch (50 mm) and Smaller: Screwed brass or iron body for 175 psig (1200 kPa) working pressure, Y pattern with 1/32 inch (0.8 mm) stainless steel perforated screen.

    - 2-1/2 inch (65 mm) to 4 inch (100 mm): Flanged iron body for 175 psig (1200 kPa) working pressure, Y pattern with 3/64 inch (1.2 mm) stainless steel perforated screen.

    - 5 inch (125 mm) and Larger: Flanged iron body for 175 psig (1200 kPa) working pressure, basket pattern with 1/8 inch (3.2 mm) stainless steel perforated screen.

  - GAS PRESSURE REGULATORS

    - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

    - Product Description: Spring loaded, general purpose, self-operating service regulator including internal relief type diaphragm assembly and vent valve. Diaphragm case can be rotated 360 degrees in relation to body.

      - Temperatures: minus 20 degrees F (29 degrees C) to 150 degrees F (66 degrees C).

      - Body: Steel.

      - Spring case, lower diaphragm casing, union ring, seat ring and disk holder: Aluminum.

      - Disk, diaphragm, and O-ring: Fluoroelastomer.

      - Maximum inlet pressure: 150 psig (1030 kPa).

      - Furnish sizes 2 inches (50 mm) and smaller with threaded ends. Furnish sizes 2-1/2 inches (65 mm) and larger with flanged ends.

  - GAS PRESSURE RELIEF VALVES

    - Furnish materials in accordance with Ministry of Public Work's and Housing standards.

    - Product Description: Spring loaded type relief valve.

      - Body: Aluminum.

      - Diaphragm: Nitrile.

      - Orifice: Aluminum.

      - Maximum operating temperature: 150 degrees F (65 degrees C).

      - Inlet Connections: Threaded.

      - Outlet or Vent Connection: Same size as inlet connection.

- 2.7 UNDERGROUND PIPE MARKERS

- Plastic Ribbon Tape: Bright colored, continuously printed, minimum 6 inches (150  mm)

- wide by 4 mil (0.10 mm) thick, manufactured for direct burial service.

- 2.8 BEDDING AND COVER MATERIALS

- Bedding: Fill Type Sweilieh.

- EXECUTION

  - EXAMINATION

    - 01300 - Administrative Requirements: Coordination and project conditions.

    - Verify excavations are to required grade, dry, and not over-excavated.

  - PREPARATION

    - Ream pipe and tube ends. Remove burrs. Bevel plain end ferrous pipe.

    - Remove scale and dirt, on inside and outside, before assembly.

    - Prepare piping connections to equipment with flanges or unions.

  - INSTALLATION - INSERTS

    - Provide inserts for placement in concrete forms.

    - Provide inserts for suspending hangers from reinforced concrete slabs and sides of reinforced concrete beams.

    - Provide hooked rod to concrete reinforcement section for inserts carrying pipe 4 inches (100 mm) and larger.

    - Where concrete slabs form finished ceiling, locate inserts flush with slab surface.

    - Where inserts are omitted, drill through concrete slab from below and provide through-bolt with recessed square steel plate and nut [above] [flush with top of] [recessed into and grouted flush with] slab.

  - INSTALLATION - PIPE HANGERS AND SUPPORTS

    - Install hangers and supports in accordance with ASME B31.9 and ASTM F708.

    - Support horizontal piping hangers as scheduled.

    - Install hangers to provide minimum 1/2 inch (13 mm) space between finished covering and adjacent work.

    - Place hangers within 12 inches (300 mm) of each horizontal elbow.

    - Install hangers to allow 1-1/2 inch (38 mm) minimum vertical adjustment. Design hangers for pipe movement without disengagement of supported pipe.

    - Support vertical piping at every floor. Support riser piping independently of connected horizontal piping.

    - Where installing several pipes in parallel and at same elevation, provide multiple pipe hangers or trapeze hangers.

    - Prime coat exposed steel hangers and supports. Finish paint exposed steel hangers and supports. Hangers and supports located in crawl spaces, pipe shafts, and suspended ceiling spaces are not considered exposed.

    - Provide clearance in hangers and from structure and other equipment for installation of insulation and access to valves and fittings.

  - INSTALLATION - BURIED PIPING SYSTEMS

    - Install LPG piping in accordance with NFPA 58.

    - Establish elevations of buried piping.

    - Establish minimum separation from other services.

    - Remove scale and dirt on inside of piping before assembly.

    - Excavate pipe trench.

    - Install pipe to elevation.

    - Place bedding material at trench bottom to provide a uniform bedding for piping, level bedding materials in one continuous layer not exceeding (100 mm) loose depth; compact to 95 percent maximum density.

    - Install pipe on prepared bedding.

    - Route pipe in straight line.

    - Install pipe to allow for expansion and contraction without stressing pipe or joints.

    - Install plastic ribbon tape continuous over top of pipe.

    - Pipe Cover and Backfilling:

    - Backfill trench.

    - Maintain optimum moisture content of fill material to attain required compaction density.

    - After hydrostatic test, evenly backfill entire trench width by hand placing backfill material and hand tamping in (150 mm) compacted layers to (300 mm) minimum cover over top of jacket. Compact 95 percent maximum density.

    - Evenly and continuously backfill remaining trench depth in uniform layers with backfill material.

    - Do not use wheeled or tracked vehicles for tamping.

  - INSTALLATION - ABOVE GROUND PIPING SYSTEMS

    - Install LPG piping in accordance with NFPA 58.

    - Provide non-conducting dielectric connections wherever jointing dissimilar metals.

    - Route piping in orderly manner and maintain gradient.

    - Install piping to conserve building space and not interfere with use of space.

    - Group piping whenever practical at common elevations.

    - Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

    - Sleeve pipe passing through partitions, walls and floors.

    - Provide clearance for installation of insulation and access to valves and fittings.

    - Provide access where valves and fittings are not exposed.

    - Where pipe support members are welded to structural building framing, scrape, brush clean, weld, and apply one coat of zinc rich primer.

    - Provide support for utility meters in accordance with requirements of utility company.

    - Install vent piping from gas pressure reducing valves to outdoors and terminate in weatherproof hood.

    - Prepare pipe, fittings, supports, and accessories not pre-finished, ready for finish painting.

    - Install identification on piping systems including underground piping.

    - Install valves with stems upright or horizontal, not inverted.

    - Protect piping systems from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.

    - Install gas pressure regulator vent full size opening on regulator and terminate outdoors.

  - FIELD QUALITY CONTROL

    - Pressure test LPG piping in accordance with NFPA 58.

  - SCHEDULES

- As per Drawings.

  - GAS LEAK DETECTION

    - Furnish materials in accordance with NFPA.

    - Gas leak detector shall be approved by local CDD

    - LPG-leak detector shall be provided, not more than 30 cm from finished floor

    - The remote emergency shut-off Switch shall be at least 1.5 m away from the appliances

    - and at the exit door(s).

    - Emergency Shut-off solenoid valve shall be directly controlled by gas detector.

PIPE HANGER SPACING

HANGER

ROD

PIPE SIZE	MAX. HANGER SPACING  DIAMETER

Inches (mm)		Feet (m)		Inches (mm)

1/2 (12)		7 (2.1)			3/8 (9)

3/4 (20)		7 (2.1)			3/8 (9)

1 (25)			7 (2.1)			3/8 (9)

1-1/4 (32)		7 (2.1)			3/8 (9)

1-1/2 (38)		9 (2.7)			3/8 (9)

2 (50)			10 (3)			3/8 (9)

2-1/2 (65)		11 (3.4)		1/2 (13)

3 (75)			12 (3.7)		1/2 (13)

4 (100)		14 (4.3)		5/8 (15)

5 (125)		16 (4.9)		5/8 (15)

6 (150)		17 (5.2)		3/4 (19)

8 (200)		19 (5.8)		3/4 (19)

10 (250)		22 (6.1)		7/8 (22)

12 (300)		23 (7)			7/8 (22)

14 (350)		25 (7.6)		1 (25)

16 (400)		27 (8.2)		1 (25)

18 (450)		28 (8.5)		1 (25)

20 (500)		30 (9.1)		1-1/4 (32)

24 (600)		32 (9.8)		1-1/4 (32)

END OF SECTION 15195

| DIVISION – 15 MECHANICAL # SECTION – 15210 | TECHNICAL SPECIFICATION MECHANICAL WORK #### EQUIPMENT BASES, SUPPORTS AND VIBRATION ISOLATION |
| --- | --- |

# PART 1	DESCRIPTION

Supports and vibration isolators for mechanical equipment.

# PART 2	PRODUCTS

2.01	Manufacturers

Subject to compliance with requirements, manufacturers offering products which may be incorporated in the Work shall conform to the required performance:

2.02	Concrete Housekeeping Pads

A.	100 mm thick minimum concrete housekeeping pads for all floor mounted equipment including casings, plenums and equipment installed on vibration isolators.

2.03	Equipment Isolators

A.	Spring:

#### 1)	Provide equipment isolator for floor mounted, low pressure packaged HVAC units; individual spring isolators with adjustable leveling bolts and anti-skid pad, arrange around perimeter of equipment to properly support load.

B.	Rubber:

#### 1)	Individual double neoprene or rubber isolators with friction surfaces top and bottom; arrange around perimeter of equipment, bolt isolators to equipment with adjustable leveling bolts.

2.04	Isolation Bases

- Rubber Rail:

#### 1)	Rail type, with slotted motor slide base, double neoprene or rubber.

- Spring:

#### 1)	Rail type fabricated of I-beam sections with slotted motor slide base and spring isolators.

- Spring Floating:

#### 1)	Isolation base shall consist of frame and spring isolators furnished as an assembly, plus a reinforced concrete inertia base, poured into the frame.  Provide for floor mounted fans and pumps over 3 kW and high pressure packaged HVAC units.

- Kinetic Floating Floor:

    - Kinetic floating floor shall consist of either roll out or jack up system designed  to NC required.

2.05	Isolation Hangers

A.	Rubber:

#### 1)	Double deflection neoprene or rubber suspension type within a steel housing.  Provide for air terminals.

B.	Combination Spring and Rubber

#### 1)	Steel compression spring and neoprene or rubber isolator unit within a steel housing.

#### Provide for suspended fans and piping within 15 m of connected rotating equipment.

2.06	Flexible Duct Connectors

A.	Refer to specification section 15910.

B.	Flexible connections shall be a minimum of 150 mm long.

# PART 3	INSTALLATION

3.01	General

A.	All equipment, piping and ductwork shall be mounted on or suspended from approved foundations and supports, all as specified, as shown, and as required. All concrete foundations including thickened structural slab, housekeeping pads and concrete for inertia pads shall be provided under this contract.

B.	Provide shop drawing and templates for all concrete foundations. Provide necessary integral steel framing, concrete reinforcing rods welded to frame, required anchor bolts, spring mountings and neoprene pads. The works to be coordinated with other operations carried out in the normal sequence on site.

C.	The foundations and vibration isolation mountings for the various equipment, piping and ductwork shall be in accordance with the requirements detailed on the Drawings and as specified.

D.	Where spring vibration isolators are called for, they shall be horizontally stable bare springs unless otherwise indicated. Static deflections shall be minimum 40mm unless otherwise indicated, and selections shall include 50% additional reserve deflection.

E.	Where a ribbed rubber assembly is called for it shall be factory fabricated from two thicknesses, unless otherwise indicated, of 6mm thick ribbed neoprene pads and shall be square in shape. Pads shall be arranged so that ribs run in opposite directions. Between each pad shall be a 1.6mm thick galvanized steel shim plate integrally and permanently bonded to the neoprene pads and base plate. The unit shall be sized so that the ribbed neoprene pads shall be loaded 150 to 200 kPa.

3.02	Mounting of Suspended Fans,  and Fan Coil      Units : (Mounting Type – 1)

- Units shall be hung spring isolators with 19mm deflection.

- Each unit not having sufficient frame rigidity shall be provided with an integral steel base for support of the suspended fan unit.

3.03	Mounting of Pumps : (Mounting Type – 2)

- Mount all base mounted pumps directly on a suitably reinforced, steel framed, concrete inertia pad which in turn shall be supported by spring isolators.

- Spring type isolators shall be free standing and laterally stable without any housing and complete with 6 mm neoprene acoustical friction pads between the base plate and the support.

- All mountings shall have leveling bolts that must be rigidly bolted to the equipment.

- Spring diameters shall be no less than 0.8 of the compressed height of the spring at rated load.

- Springs shall have a minimum additional travel to solid equal to 50% of the rated deflection.

- Submittals shall include spring diameters, deflections, compressed spring height and solid spring height.

3.04	Water Piping in Mechanical Room and pump room : (Mounting Type – 3)

A.	Piping shall be hung from resilient hangers.

B.	These hangers shall be combination rubber-in-shear and spring hangers.

C.	The spring in each such hanger shall have an initial deflection of 25mm under the installed load.

3.05	Mounting of Centrifugal Exhaust and Ventilation Fans : (Mounting Type – 4)

- Fans shall be mounted on structural steel rail with spring isolators have an initial deflection of 19mm.

3.06	Mounting of AXIAL FANS:

- Fans shall be mounted on structural steel rail with spring isolators have The springs shall have an initial deflection of 38mm.

### MOUNTING OF Outdoor VRF units and package unit:

- Mount all base mounted units on a Curb-mounted base with 19mm minimum deflection spring isolators.

- Submittals shall include spring diameters, deflections, compressed spring height and solid spring height.

3.08	Flexible Duct Connectors

A.	Flexible connections to prevent the transmission of vibration through the ducts shall be installed on both the supply and return sides of all fans and ventilation units approximately where shown on the Drawings.

END OF SECTION 15210

| DIVISION – 15 MECHANICAL SECTION – 15291 | TECHNICAL SPECIFICATION MECHANICAL WORK HVAC THERMAL INSULATION |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical specification establishes the type and quality of materials and the standard of workmanship to be used in the supply and application of thermal insulation for HVAC items.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and application of thermal insulation as specified herein and where referred to on the Drawings.

B.	Coordination: The Contractor shall be responsible for the full coordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	Manufacturers: Firms regularly engaged in the manufacture of thermal insulation materials whose products have been in satisfactory use for a similar application for not less than 10 years.

B.	Installer: Firms regularly engaged and qualified in the application of thermal insulation materials with at least 5 years successful installation experience on projects of a similar nature.

C.	No thermal insulation shall be applied to pipe work and ductwork services until the installations have been inspected by the Engineer and tested in accordance with the relevant sections of this specification.

1.04	APPLICABLE CODES AND STANDARDS

A.	The thermal insulation products and all associated materials shall comply with the latest relevant British Standards in all respects.

B.	The following are the most commonly used and relevant British Standards associated with thermal insulation products and associated material. However, the Contractor shall ensure that all applicable British and International  Standards are complied with whether listed here or not.

BS 476 Part 4:		Non-combustibility Test for Materials.

BS 476 Part 7:		Method for Classification of the Surface Spread of Flame of Products

BS 476 Part 20:	Method for Determination of the Fire Resistance of Elements of Construction.

BS 1485	:	Specification for Zinc Coated Hexagonal Steel Wire Netting.

BS 3958 Part 3:	Metal Mesh Faced Man-made Mineral Fibre Mattresses.

BS 3958 Part 4:	Bonded Preformed Man-made Mineral Fibre Pipe Sections.

BS 3958 Part 5:	Specification for Bonded Man-made Mineral Fibre Slabs.

BS 5422	:	Specification for the use of Thermal Insulation Materials.

BS 5970	:	Code of Practice for Thermal Insulation of Pipework and Equipment.

1.05	SUBMITTALS

A.	Drawings refer to 15010

B.	Products: Full manufacturers data confirming type and composition of all products including thermal characteristics.

C.	Samples - Section of insulated duct

- Section of insulated pipe

Both showing detail of resilient spacer at bracket location.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with 15010

1.07	WARRANTY

A.	Provide 12 months warranty in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	GENERAL

A.	For general applications the thermal insulation materials shall be made from non-combustible materials. On the other hand, materials that are not entirely non-combustible may be accepted if they have self-extinguishing characteristics, the total mass of combustible materials is small and combustion does not produce dense smoke or toxic fumes. All material finishes shall conform to spread of flame classification class “A” according to NFPA101. Such materials shall only be used with the prior permission of the Engineer.

B.	Insulation shall be rotproof, odourless, non-hyroscopic, shall not sustain vermin and shall not contribute to metal corrosion. Any finishes (or coverings) used shall not deteriorate with age or the effects of solar heat.

C.	Thermal insulation materials and their finishes shall be asbestos free and be suitable for continuous use throughout the range of operating temperatures and within the environment indicated.

D.	All insulating materials and associated products, sealants, tapes, adhesives, securing bands and protective cladding shall be as specified or equal and approved.

2.02	DUCTWORK INSULATION

- Thermal insulation of rectangular ductwork running on roof shall be rigid rockwool (ductslab) mineral fibre slab consisting of long fine fibres (free from short and coarse fibres) bonded with a temperature resistant resin. The density shall be a minimum of 45-48 kg/m3.

- Thermal insulation of rectangular ductwork running above false ceiling shall be flexible rockwool (ductwrap) mineral fibre consisting of long fine fibres (free from short and coarse fibres) bonded with a temperature resistant resin. The density shall be a minimum of 45-48 kg/m3.

- Thermal insulation of circular ductwork shall be flexible rockwool mineral fibre material consisting of long fine fibres (free from shot and coarse fibres) made up in mat form. The density shall be a minimum of 32 kg/m3.

- Thermal insulation on ductwork etc. inside buildings (above conditioned space) generally shall be at least 25mm thick where its declared value of thermal conductivity at the relevant temperature is equal to or less than 0.04 W/m.K , In the open air, in plant rooms and in large unconditioned open areas of buildings, the thermal insulation shall be at least 50mm thick where the thermal conductivity is less than or equal to 0.04 W/m.K. Insulation shall be covered with 0.5mm hot dipped Galvanized steel sheet G90. Fixed and installed in accordance with BS5790.

- All ductwork thermal insulation shall be complete with a reinforced aluminium foil applied to one side during the manufacturing process.

- The whole to be further supported by means of:-

    - 19 - 22 swg x 50 mm mesh galvanised wire netting. Care to be taken when applying wire mesh support to avoid damaging the aluminium foil.

Or

    - Aluminium Bands, circumferential at nominal 300 mm centres. Bands located over the outer surface typically 50 mm from the circumferential joint of the rockwool Ductwrap and Ductslab. Do not over tighten the aluminium bands, as this will locally reduce the thickness of the insulation and reduce the thermal efficiency.

Where support pins/hangers puncture the foil, they should be sealed using aluminium foil tape to maintain the vapour barrier.

.

- Where an acoustic lining to ductwork is specified, it shall be closed cell type   Elastomeric foam based synthetic rubber.Material shall have self adhesive coating; pressure-sensitive adhesive coating on modified acrylate basis with mesh structure and covered with polyethylene foil. Thermal conductivity shall be 0.036 W/moC As minimum. Thickness shall be 12mm as minimum and final thickness shall be selected to match noise reduction required.

2.04	REFRIGERATION PIPEWORK INSULATION

- Thermal insulation shall be preformed un-slit foamed Class 1 plastic material to suit the size of the pipe. The vapour barrier shall be an integral part of the material. The insulation shall have a thermal conductivity of 0.0375 W/moC and shall be satisfactory for a temperature range of 0oC to 104oC without deformation or deterioration. The minimum thickness of the insulation shall be 25mm.

# PART 3 EXECUTION

3.01	STORAGE

A.	All thermal insulation materials shall be stored in their original packaging in such a manner as to prevent the ingress of dust or moisture. The height of the packages shall be restricted to prevent any deformation of preformed rigid sections.

B.	Flat sheet and rolled metal materials used for protective claddings shall be stored away from the ground surface, adequately covered and protected in a manner to prevent damage to the materials.

C.	All storage areas shall have adequate lighting to allow for the inspection of all materials.

3.02	FIXINGS

A.	All mechanical fixings (rivets, screws) shall be as recommended by the manufacturer of the material being fixed. All mechanical fixings, sealants, tapes and adhesives shall be entirely suitable for the medium that they are being applied to and the application shall be fully in accordance with the manufacturers recommendations.

3.03	DUCTWORK INSULATION

A.	Thermal insulation to ductwork shall be carried out neatly and to a high grade quality by skilled workers experienced in the trade, and strictly in accordance with this Specification. No thermal insulation shall be applied to any ductwork prior to completion of any air leakage testing that may be required and only then after a full inspection and approval by the Engineer.

B.	Thermal insulation shall be applied to all supply and return ductwork carrying conditioned air through unconditioned areas including plantrooms. Thermal insulation shall not be installed on the sections of return air ductwork covered with fire resistant cladding.

Supply ductwork carrying conditioned air through conditioned areas shall be insulated, whereas return ductwork passing through conditioned areas shall be insulated  as well . Fresh air duct and Exhaust duct (clean) work shall be insulated.

All ductwork exposed to the atmosphere shall be insulated and protected by galvanized steel cladding.

C.	Where ductwork passes through masonry walls, floors and roofs a sheet metal sleeve shall be installed and the gap, equal to the insulation thickness, shall be packed with a load bearing insert with integral vapour seal. The thermal insulation shall be butt jointed to the insert and the joint sealed by the use of 75 mm wide aluminium tape. All openings through external walls and roofs shall be fitted with a flashing fixed to ensure water will not enter the insulated space between the ductwork and the cladding.

D.	Where the insulation is 50 mm thick or more (except for insulation which is sprayed or moulded in situ) the insulation shall be fixed in two layers with joints staggered. For air heaters using media at high temperature the thermal insulation material shall be suitable for use at those temperatures.

E.  Until final acceptance of the installation by the Engineer, the Contractor shall make good any damage to insulation at his own expense, so that the installation is handed over in a perfect conditioned.

F.	All attenuators and diffuser plenums shall be insulated and vapour sealed to the same specification as the ductwork connecting to them except diffuser plenum boxes specified as having internal acoustic/thermal insulation.

3.04	PLANT AND PIPEWORK INSULATION

A.	Thermal insulation to pipe work shall be carried out by specialists and strictly in accordance with this Specification.  No thermal insulation shall be applied to pipe work prior to witnessing of the pipe work pressure test. Only then, and after a full inspection and approval by the Engineer, the insulation could be applied.

B.	Thermal insulation shall be applied to the following:-

- External distributing mains and fittings above ground and in ducts, chases and trenches including all valve bodies and flanges.

(ii)	Buried pipe work shall have special forms of insulation as indicated.

(iii)	All condensate drainage pipe work to prevent shedding of condensation.

Insulation shall fit closely on pipe work and other surfaces without gaps between.

C.	All sections of the insulation shall be of the correct size and made for the type and grade of piping to which it is fitted and shall form a tight fit on the pipe work after application of adhesive and lapping.

D.	At all instrument points or tapings on pipe work or ductwork the insulation shall be cut away and the edges neatly finished and sealed as for adjacent finishes allowing access for the instrument.

3.05	REFRIGERATION PIPEWORK INSULATION

A.	The suction line from the evaporator to the compressor shall be insulated with foamed plastic as specified previously and shall be protected by a vapour barrier which shall not be broken between joints of sectional material or at discontinuities of valves or brackets.

B.	Where possible the insulation shall be sleeved on the pipes before they are fitted. At all junctions, elbows, valves, and the like, it shall be carefully cut and fitted to the method recommended by the manufacturer.

C.	All open edges, joints and the like, shall be sealed with an adhesive as recommended by the insulation manufacturer.

3.06	PROTECTION

A.	The Contractor shall take all necessary measures to protect the works during construction. Any damaged sections of insulation shall be completely cut out and replaced with a new section. The vapour seal shall be repaired to ensure continuity.

All damaged sections shall be replaced at the Contractor's expense until the system is accepted and finally handed over.

END OF SECTION 15291

| DIVISION – 15 MECHANICAL SECTION – 15310 | TECHNICAL SPECIFICATION MECHANICAL WORK FIRE PROTECTION SYSTEM |
| --- | --- |

1.01	SCOPE OF SECTION

A.	This technical specification establishes the minimum requirements for the equipment to be incorporated into the infrastructure and above ground fire protection pipe work.

1.02	WORK INCLUDED

A.	Provision of all labour, materials, and the performance of all operations necessary for the supply and installation of pipe work, controls and equipment of the Fire Water Systems as specified herein and as detailed on the Drawings.

B.	Coordination:  The Contractor shall ensure that the Fire Water Systems are fully compatible with all trades, particularly those of the Civil, Mechanical and Electrical services, for successful installation and operation.

C.	Submittals: The Contractor shall submit to the Engineer for review and approval, all calculations and drawings for the equipment proposed and associated builders works to show that the plant as installed will meet all the specified criteria.

No works shall commence on the production of the package or associated site works until the design has received the approval of the Engineer.

1.03	APPLICABLE CODES AND STANDARDS

A.	The Fire Water System shall comply with the latest relevant National Fire Protection Association (NFPA) codes and standards in all respects.

B.	The following are the most commonly used NFPA standards associated with Fire Water Systems. However, the Contractor shall ensure all applicable NFPA standards are complied with, whether here or not.

NFPA 1	-	Fire Prevention Code.

NFPA 54	-	National Fuel Gas Code

##### ANSI B73.1	-	Specification for Horizontal End Section Centrifugal Pumps

UL	-	Underwriters Laboratory

FM	-	Factory Mutual

1.04	SUBMITTALS

A.	Drawings - refer to Section 15010

B.	Products - submit full manufacturers data for every item.

C.	Provide samples of pipe work showing each type of joint to be used.

D.	Full systems Calculations.

1.05	OPERATION MAINTENANCE DATA

A.	Comply with Section 15010.

1.06	WARRANTY

A.	Provide 12 month warranty from the date of taking over certificate in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	GENERAL

A.	Pipe work and fittings shall be as specified or approved equivalent and shall be manufactured fully in accordance with the relevant Codes and Standards.

B.	Pipe work and fittings that have been subject to corrosion or damage shall not be acceptable.

C.	All goods and products shall be new and free from any surface rust or mill scale.

D.	All individual lengths of pipe work or individual valves shall be stamped with their manufacturers name, place of origin, size and class of duty.

E.	All pipe work and fittings (screwed and flanged) shall be suitable for the working pressure, operating temperatures and conditions of the fluids flowing within them. The declared pressure rating of the pipe work shall be equal to or greater than the maximum test pressure of the system.

F.	The working pressure for pipe work, connections and fittings is based on the total static pressure in the pipe work in addition to the operating pressure exerted by the pumps on the system. All Fittings and valves shall have 1.5 pressure rating of the system, taking into consideration pump close discharge pressure.

2.02	ABOVE GROUND PIPING

A.	Pipe work shall be seamless black steel schedule 40 according to ASTM A53.

B.	All fittings shall be Gray Iron Threaded Fittings, Classes 125 and 250.

C.	Bends and swept tees shall be used throughout. The use of elbows will not be permitted and square tees will be allowed only where vent connections are taken off.

# PART 3 EXECUTION

3.01	INSPECTION OF FIRE SERVICES PIPEWORK

A.	The Contractor shall inspect all products for damage immediately before installation. Any products that are damaged or not in accordance with this Specification shall immediately be repaired or removed from the site and replaced.

3.02	HANDLING OF FIRE SERVICES PIPEWORK

A.	All pipes, and piping accessories shall be inspected at time of delivery for damage and for compliance with this Specification.

B.	Any products that are damaged or found not to be in accordance with this Specification shall be immediately repaired or replaced. Such repairs shall be done only after the approval of the Engineer.

C.	All products shall be handled and stored as recommended by the manufacturer to prevent damage and deterioration.

D.	The Contractor shall supply handling equipment such as lifting beams, reinforced cranes are used, protective padding, struts, cradles, etc., required to install products without damage.

E.	The Contractor shall unload all products singly from trucks or lorries. Unless cranes are used, pipes shall be unloaded by means of skids and check ropes and no pipe shall be dropped.

F.	Each pipe unit shall be site stored, stacked and handled into its position in the trench only in such manner, and by such means, that affords total protection for it from damage of any kind. Site stacking of pipe work shall be such that the pipe work shall not deform or be damaged in any way through storage or retrieval. The manufacturer's recommendations shall be taken as the minimum requirements.

3.03	SCREWED PIPEWORK

A.	All pipework 50mm and below shall be screwed except where it is permanently concealed.

The threading of screwed joints shall be carefully made and shall be cut to produce an accurate thread free from burrs, snags and swarf. At least one of the engaging components shall be taper threaded.  All ends of pipe shall be reamed to restore full bore prior to assembly.  Subject to these provisions, threading may be carried out by hand or by automatic machine.

B.	Screwed joints shall be made using P.T.F.E. tape. Joints shall be pulled up tightly and all extruded jointing material shall be removed and the joint left clean.

C.	Where pipes are held in vices for threading, care shall be taken to ensure that the pipe surface is not damaged.  Any pipework so damaged shall not be fitted.

D.	All pipework joints shall be cleaned thoroughly to remove traces of tape prior to painting with a final coat of red oxide.

3.04	PAINTING OF PIPEWORK AFTER INSTALLATION

A.	All ferrous surfaces to be wire brushed and painted with three coat of red oxide paint after installation.

3.05	SYSTEM TESTING OF FIRE SERVICES PIPEWORK

A.	General:

1.	The Contractor shall ensure that all pipework is watertight to the satisfaction of the Engineer and shall supply all pressure gauges, meters, hoses, pumps and all temporary supports, equipment and manpower necessary for carrying out pressure tests.

2.	The Contractor shall, during testing, check the satisfactory operation of each valve and hydrant installed under the Contract.

B.	System Test:

1.	Before filling or pressure testing is started the Contractor shall re-check pipes and valves for cleanliness and shall re-check the operation of valves. The open ends of the pipes shall normally be stopped off by blank flanges or capped ends additionally secured where necessary by temporary struts and wedges.

2.	Fire water systems shall be suitable for the working pressure, operating temperatures and the conditions of the fluids flowing within them. the declared pressure rating of the pipework shall be equal to or greater than the maximum test pressure of the system. The testing shall be carried out in sections if necessary. If a section should fail the test, the Contractor shall trace and repair all leaks and defects and retest the section before any further pipes or section of adjacent pipework are laid.

3.	The working pressure for pipework connections and fittings is based on the total static pressure in the pipework in addition to the operating pressure exerted by the pumps on the system.

4.	The system shall be filled with potable water and all air expelled. After the system has been completely filled, the pressure shall be steadily and gradually increased until the test pressure has been reached. if any loss is recorded, repairs shall be made and the test re-run.

C.	Test Results:

Upon completion of the tests, written records of every test clearly identifying the tested section of the pipe together with time of test and name of testing engineer in tabulated format shall be submitted to the Engineer for review.

3.06	FLUSHING AND DISINFECTION

A.	Fire services pipelines shall be flushed with potable water after completion of pressure testing and before disinfections.

B.	Liquid chlorine, calcium hypo chlorite or sodium hypo chlorite shall be used for disinfections. Where liquid chlorine is used, it shall be introduced only in conjunction with proper equipment and under the supervision of qualified personnel familiar with the physiological, chemical and physical properties of liquid chlorine and who are suitably trained and equipped for dealing with any emergency which may arise from its use.

C.	Fire service water from a suitable source shall be injected with flow control at a constant and measured rate. The water shall receive a dosage of chlorine fed at a measured constant rate to ensure chlorine concentration in the water entering the pipe is maintained at a minimum of 50mg/1. The chlorine residual shall be measured at regular intervals to ensure that the required chlorine concentration is maintained.

D.	During the application of chlorine, valves shall be manipulated to prevent the treatment dosage from flowing back into the line supplying the water. Chlorine application shall continue until the entire pipeline is filled with chlorine solution.

E.	After 24 hours retention, the heavily chlorinated water shall be flushed out with potable water, until the chlorine concentration in the water leaving the pipeline does not exceed 1 mg/1. Chlorine residual determination shall be made to ascertain that the heavily chlorinated water has been removed from the pipeline.

F.	Flushing water shall be discharged only to sites or into conduits. Discharges, which cause damage, create nuisance or health hazard, or interfere with the work of others will not be permitted.

3.07	VALVES

Refer to section 15411

  - HOSE REEL CABINET

The cabinet and door leaf shall be made of 1.5 mm steel sheet with all around

folded edges, door leafs hinged flush mounted or doorframe. The cabinet shall

be equipped with vertical wired glass window on front door. The cabinet shall

be painted red with electrostatic powder paint. The cabinet shall be complete

with the water connections placed to suit the supply pipes. The door shall be

recessed type with aluminum turn handle chrome plated.

The cabinet shall consist of the following:

- Hose reel.

- 6 kg dry powder Potable Fire Extinguisher

Cabinet shall be equipped with 30 m of 25 mm UL, FM rubber hose suitable for a working pressure of 1034 kPa mounted on a revolving drum. Lever operated control nozzle of 6 mm orifice, swing type with jet/spray. The reel to be fitted with an automatic valve to operate when 3 metres of hose is unwound. The drum shall be painted red. The reel shall be supplied complete with cabinet with water connection placed to suit the supply pipe.

  - PORTABLE FIRE EXTINGUISHERS

A.	Portable Fire Extinguishers shall be of the type indicated on the drawings and specified herein.

B.	The fire extinguishers shall conform to the requirements of NFPA 10 for design standard and performance with the classes of fire as defined in that standard and this Specification.

C.	Classes

Class A	Fire involving solid materials, usually of an organic nature such as wood, cloth, paper, rubber and many plastics.

Class B	Fires involving flammable liquids, oils, greases, tars, oil based paints, lacquers and flammable gases.

Class C	Fires involving energized electrical equipment where the electrical non-conductivity of the extinguishing media is of importance.

D.	Multi-purpose dry powder (chemical)-Class A.B. and C fires. Multi-purpose dry powder extinguishers shall be ammonium phosphate, stored pressure type with steel cylinders, braided PVC or black reinforced rubber discharge hose and nozzle and pressure gauge. Suitable carrying handles shall be incorporated in the extinguisher body or the control mechanism moulding. Extinguishers shall be hermetically seated to prevent moisture contaminating the powder.

E.	Carbon Dioxide (CO2) - Class B and C fires. Carbon Dioxide extinguishers shall have steel cylinders and be complete with swivel horn or hose and horn applicator.

F.	Water (H2O) - Class 'A' fires water extinguishers shall be stored pressure type with steel cylinders, braided PVC or black reinforced rubber discharge hose and nozzle and pressure gauge. Suitable carrying handles shall be incorporated in the extinguisher body or the control mechanism moulding.

G.	Foam - Class A and B fires. Foam extinguishers shall be of the stored pressure type with steel cylinders, braided PVC or black reinforced rubber discharge hose and nozzle and pressure gauge. Suitable carrying handles shall be in corporated in the extinguisher body or control mechanism moulding.

H.	Special Features

All portable extinguishers shall be wall bracket mounted as shown on the drawings.  Wall mounted units shall be supplied complete with purpose made wall brackets, and the Contractor will secure these to the building structure so that the installed height of each extinguisher conforms to the NFPA Standard 10 Clause 1-6.9 relative to its gross weight.  Where floor standing units are provided these shall be fitted with integral steel skirts such that the extinguisher body itself does not rest on the floor.  Specific extinguisher requirements are shown on the drawings.  Where concealed mounting is required the extinguisher shall be provided with all accessories required for such mounting.

All types of extinguisher shall be fitted with a locking pin arrangement to prevent accidental discharges, the safety pins being secured to the unit by a chain or wire cable to prevent loss.

I.	Design, Deployment and Capacity

The extinguisher designs shall be such as to facilitate inspection, cleaning, repair and replacement, and be simple and reliable when in use under operational (or training) conditions.

The mounting requirement for extinguishers shall be as shown on the Drawings.  The Contractor shall not deviate from this requirement or other aspect of the specification without the permission of the Engineer.

The locations, type of extinguishant and capacity of fire extinguishers are shown on the relevant Drawings.  The capacity of each unit specified is the minimum quantity of extinguishant required at the location indicated.  The Contractor may supply slightly larger sizes to that specified where the Specification does not coincide with a particular supplier's production standard extinguisher.  If the nearest standard deviates considerably from the Specification the Contractor shall obtain the approval of the Engineer before placing his order.

J.	Extinguisher Marking

All extinguishers shall carry in English and Arabic clear and concise operating instructions and warnings against use on fires for which the extinguishant is not suitable, or any other warnings of which the operator must take heed.  The extinguisher class suitability and warnings may take the form of pictorial labels as depicted in the NFPA Standard 10.

The following information shall also be clearly marked on the body of each unit:

1.	The name of the manufacturer.

2.	Instructions for regular periodic checking of the units for operational serviceability.

K.	Portable Fire Extinguishers - Types and Sizes

1.	Multi-purpose dry powder complete with wall bracket.

Capacity			6Kg		10Kg

Range & discharge		5-7m		5-7m

Duration of

discharge			13 secs	20secs

Blocked nozzle

pressure at 20oC		13 bar		13 bar

2.	Carbon Dioxied

Capacity 			           3 kg		5 kg		6 kg

Minimum range of discharge	3 m		5 m		3 m

Duration of discharge		17 secs.	15 secs.	17 secs.

Working pressure		           50 bar		50 bar		50 bar

at 20C

3.	Foam

Capacity			           6 L		9 L

Minimum range of discharge	4 m		4 m

Duration of discharge		28 secs.	40 secs.

Working pressure		         12.5 bar	12.5 bar

at 20ºC

4.	Water

Capacity			          10 L

Minimum range of discharge	6 m

Duration of discharge		65 secs.

Working pressure at 20C                         12.5 bar

END OF SECTION 15310

| DIVISION – 15 MECHANICAL # SECTION – 15410 | TECHNICAL SPECIFICATION MECHANICAL WORK PLUMBING PIPING |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical Specification establishes the minimum requirements for the equipment to be incorporated into the above ground Soil, Waste and rainwater and hot and cold water services plumbing pipework.

It also establishes the quality of materials and workmanship to be used in the supply and installation of the systems.

1.02	WORK INCLUDED

A.	Provision of all labour, materials and the performance of all operations necessary for the supply and installation of pipework and fittings of the soil and waste systems as specified herein and as detailed on the Drawings.

B.	Coordination:  The Contractor shall ensure that the soil and waste systems are fully compatible with all trades, particularly those of the Civil, Mechanical and Electrical services, for successful installation and operation.

C.	Submittals:  The Contractor shall submit to the Engineer for review and approval, all calculations and drawings for the equipment proposed and associated builders works to show that the plant as installed will meet all the specified criteria.

No works shall commence on the site until the design has received the approval of the Engineer.

1.03	QUALITY ASSURANCE

A.	Manufacturers:  The contractor shall only propose the use of materials produced by firms who have been regularly engaged in the manufacture of plumbing pipework systems and whose products have proved satisfactory in similar service for not less than 10 years.

B.	Installer:  Firms proposed for the installation of the plumbing pipework systems shall have been regularly engaged for at least 5 years in the installation of plants of a similar type, quality and scope as is required for this project.

1.04	APPLICABLE CODES AND STANDARDS

The plumbing pipework shall comply fully with the latest relevant British and International  Standards in all respects.

B.	The following are the most commonly used and relevant British International Standards associated with Soil and Waste Systems. However the Contractor shall ensure that all applicable British, International Standards are complied with, whether listed here or not.

BS: 3380   -	Wastes (excluding skeleton sink wastes) and bath overflows.  In conjunction with BS 2779, 3643 and 5572.

BS: 3505   -	Specification for uPVC pressure pipes.

BS: 3943   -	Plastic waste traps.  In conjunction with BS 2779 and    3380.

BS: 3974   -	Pipe supports.

(Part 1 & 2)

BS: 4118   -	Glossary of sanitation terms.

BS: 4514   -	Unplasticized PVC soil and ventilating pipes, fittings and accessories.

BS: 4576   -	Unplasticized PVC rain water goods.  In conjunction with BS 2494 Part 2, 4514.

BS: 4660   -	Unplasticized PVC underground drain pipe and fittings.  In conjunction with BS 2494, 5955 and CP312.

BS: 5255   -	Plastic waste pipe and fittings.  In conjunction with BS 21, 2494, 2779 and 4515.

BS 5911      -	Plain and reinforced concrete pipes and fittings.

BS 843      -	Thermal-storage electric water heaters. In conjunction with BS 3456, Sections 2.21, 2.7 an 3.9 and 3999 Part 2.

BS 1010   -	Specification for drains off taps and stop valves for water services.

BS 2494   -	Elastomeric joint rings for pipework and pipelines. In conjunction with BS 1179, 3502, 3574, 4250, and 4947.

BS 2779   -	Pipe threads. for tubes and fittings where pressure-tight joints are not made on the threads

BS 3284   -	Polythene pipe (type 50) for cold water services. In conjunction with BS 21 and 5556.

BS 3505   -	uPVC pressure pipes for cold potable water. In conjunction with BS 21 and CP 312.

BS 3605   -	Seamless and welded austenitic stainless steel pipes and tubes for pressure purposes. In conjunction with BS 3600.

BS 3955   -	Electrical controls for household and similar general purposes

BS 3974   -	Pipe supports.

Part 1 & 2

BS 4346   -	Joints and fittings for use with uPVC pressure pipes. In conjunction with BS 3505, 3506, 4576, 4660, 5481 and 6209.

BS 4368   -	Compression coupling for tubes. In conjunction with BS 1706, 2051, 2779, 2871, 3601, 3602, 3605, 3643, 4368 and Din 2353.

BS 5114   -	Performance requirements for joints and compression fittings for use with polyethylene pipes. In conjunction with BS 1972, 1973,2494 and 3284.

BS 5433   -	Underground stop valves for water services. In conjunction with BS 21,61,864, 1972, 3284, 3885 and 5728 Part 1 and 2.

BS 6281   -	Devices without moving parts for the prevention of contamination of water by backflow. In conjunction with BS 864, 2779, 2872, 4504, 5412 and 5413.

BS 1387   -	Galvanised steel medium and heavy duty.

BS 6675   -	Servicing valves (copper alloy) for water services. In conjunction with BS 864, 1400, 2871, 2872 and 2874.

BS 6700   -	Design, installation, testing and maintenance of services supplying water for domestic use within buildings and their curtilages.

BS: 5481   -	Unplasticized PVC pipes and fittings for gravity sewers.  In conjunction with BS 2494, 4660 and CP 312.

BS: 5572   -	Sanitary pipework.   In conjunction BS 416, 437, 1188, 1387, 1710, 1973, 2871, 3506, 3868, 4118, 4514, 5254, 5255, CP3.

BS: 6283   -	Safety devices for use in hot water systems.  In conjunction with BS 864, 2056, 2779, 2872, 2874, 3075, 3457, 4504, 5412 and 5413.

BS: 8000   -	Part B Section 3 - Above ground drainage

BS: 6367   -	Drainage of roofs and paved areas

DIN:8062  -   Drainage pipes with solvent welding socket Series 5, PN16 bar              UPVC pipes.

DIN:1953 & 19534 – UPVC sewage & drainage pipes with rubber ring socket.

BS:2871      -      Specification for copper tubes for water, gas and sanitation,

table-X.

BS:416       -      Specification for cast iron spigot and socket soil, waste and

ventilation pipes.

BS:437	      -       Specification for cast iron pipes and fittings.

In addition to the above standards the works shall be in accordance with all local bye-laws, local municipality requirements and the manufacturers recommendations.

1.05	SUBMITTALS

A.	Drawings - refer to Section 15010

B.	Products - submit full manufacturers data for every item.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with Section 15010.

1.07	WARRANTY

A.	Provide 12 month warranty in accordance with contract conditions.

PART 2 PRODUCTS

2.01	SOIL WASTE AND RAINWATER PIPEWORK

A.	Pipework and fittings

1.	All main soil, waste and rainwater stack pipes shall be  installed in UPVC 10 bar according to DIN 8061/ 8062 standard.

2.    All drainage pipes above false ceiling within occupied spaces and toilets of guest rooms shall be used low noise drainage pipes .

B.	Vent / antisiphon pipework

1.	All vent and antisiphon pipework pipes shall be installed in UPVC pipework except that of kitchen.

2.	The jointing of the UPVC pipework and fittings shall be by the use of solvent weld sockets and shall be carried out in full compliance with the manufacturer's recommendations.

3.	Expansion joints and pipe support brackets shall be installed in accordance with the manufacturer's recommendations and BSCP312.

4.	Sleeves shall be provided where pipes pass through walls or floors to allow free axial movement of the pipes.  Sleeves shall be of a material compatible with the pipes they protect, non combustible and two pipe sizes larger than the pipe being protected and packed with mineral .

5.	Where such pipes pass through fire compartment walls, floors or ceiling cavity barriers the pipes shall be installed with fire sleeves.

C.	PVC branch soil waste and vent pipework

1.   The soil, waste and vent pipework shall be UPVC class 4 to DIN.

- The UPVC soil waste and vent pipework shall have solvent joints in general, with expansion joints where specified.

- All drainage pressure pipes and fittings shall be PN16 according to DIN 8062.

4.	All pipe work shall be adequately supported at the centers indicated in Table 13 of BS5572. All PVC pipework shall be supporting with extension expanding ragbolt fixings in the brickwork.  Where the brackets are to be used as anchor points they will be made to grip the pipe by means of a rubber sleeve, and must support the pipe with additional studding and back plates to the duct wall.  All horizontal waste pipework shall be supported on the manufacturer's screw-to-wall brackets.

5.	All waste pipes shall fall from fittings to their respective main soil pipe so as to be self-draining.  Branch vent pipes shall rise towards their respective main vent pipe so as to be self-venting.

6.	All branch waste pipes to a range of fittings shall have an access provided on the pipe in an accessible position at the end of the run.  All traps shall be adequately ventilated in order that the seal may be maintained.

7.	Water closets shall be connected by flexible self sealing w.c. "Multikwik" connector, and shall be discharged into adjacent soil pipe.

D.	PVC traps

1.	All basins shall be provided with an appropriately sized PVC ‘’P’’ trap.

2.	All sinks, etc, and other mechanical and specialist items of equipment, shall be provided with an appropriately sized white PVC "P" trap (unless such specialist item of equipment is supplied with its own integral trap).

3.	Traps to be chrome plated where exposed to view, and in these situations a chrome plated cover plate shall be provided to mask the penetration of the waste pipe through the duct wall or structure.  Approval shall be obtained from the local Public Health Authority of all types of traps that are intended for installation.  All traps shall have a 75 mm water seal.

2.02.	POTABLE COLD AND HOT WATER SERVICES

- PIPEWORK AND FITTINGS

1.	Pipes:

- UPVC  or CPVC Pressure Pipes and fitting manufactured to DIN standards or BS.

- Galvanized steel pipe work to BS 1387 medium class.

- Cross liked polyethylene pipe work  XLPE to DIN standard . XLPE pipe work shall be DVGW, KIWA approved.

- HDPE Pressure Pipes and fittings for underground and outdoor

(municipality) manufactured to DIN standards PN 20.

- Polypropylene  random copolymer pipework to EN-ISO15874.

- SYSTEM DESCRIPTION

1.	This section relates to the installation of potable cold water systems at all facilities.

2.	Incoming pipeline from the municipality water mains shall be provided with a water meter located in an area free of wheeled access, but positioned to enable the meter to be read without entering the building served by the metered connection. The location shall be as shown on drawings.

3.	Internal Potable Water Installation:

All cold water supply piping inside the building from risers to cabinet shall be made of PPR PN 20 class 1 pressure pipe unless otherwise indicated on relevant drawings. All hot water piping from risers to cabinet shall be PPR PN 20  class 2 pressure pipe. All cold and hot water pipe work connection to fixtures shall be PEX. Main cold water risers shall be galvanized steel 1387 medium class. All soft water pipes shall be CPVC PN20 to DIN.

- PIPEWORK SUPPORTS

Pipework supports and hangers will comply with Section 15412.

- Thermal insulation shall comply with Section 15291. All GSP hot water pipes shall be insulated.

- Pipes on roof shall be cladded with G90 galvanized steel hot dipped sheet.

PART 3 EXECUTION

3.01	SOIL WASTE AND RAINWATER PIPEWORK

A.	Workmanship

1.	Materials and workmanship to be of best quality and executed in accordance with the Specification, drawings and manufacturers recommendations.

2.	Where any pipe is required to be shortened it shall be cut off square and cleanly with an approved pipe-cutting machine.

3.	Where special joints or jointing materials are shown for pipes of any materials, they shall be of an approved type and manufacture, and the joint shall be made in accordance with the manufacturer's instructions, or as directed.

4.	Responsibility shall be assumed to identify and install all necessary expansion couplings and fire sleeves throughout the installations.

5.	All plant, pipes and fittings etc shall be thoroughly cleaned of all foreign matter before installation.  Each section of the installation shall be clean and free from any obstructions whatsoever before proceeding with the next section of the installation.

6.	All vertical soil, waste and vent pipes are to have access doors provided on each floor, above flood level of fittings served.  Access to be provided in ducts to sanitary services.  All vent pipes are to terminate 300 mm above roof level, with suitable weathering slate apron and vent cowl or copper wire balloon.

7.	Flexible joints are to be provided wherever pipes cross expansion joints.

8.	All soil, waste, vent and rainwater pipes shall be the size and positions indicated on the drawings to take the discharge from the branch waste and vent pipes, sanitary fittings and equipment adjacent thereto.

9.	On completion the whole of the work is to be handed over in a sound and clean condition.  In the event of any pipe being fractured from any cause whatsoever after having been (to all appearances) properly installed, responsibility shall be assumed in every instance and any such defective pipes shall be replaced for approval.

10.	All pipework shall be erected to present a neat and orderly appearance, arranged parallel to or at right-angles to the structural members of the buildings, giving maximum headroom and shall not obstruct windows or doorways.  Pipes shall bend round piers, projections and into recesses forming part of the structural works whether so indicated on the drawings or not.  Pipework shall be erected such that there is a minimum clearance of 75 mm to finished floor level and a minimum clearance of 25 mm to finished wall faces.

11.	Slopes of drainage system (gravity) shall be a minimum of:

Foulwater - 1%

Drain and rainwater pipes - 1%

B.  	The discharge pipework shall be so installed as to minimize the risk of blockage.  Access covers and/or rodding eyes are to be positioned such as to enable maintenance equipment to be inserted into the system(s) to permit cleaning or clearing of all sections of the system(s).

The pipework system and fittings are to be installed so that broken or defective parts can be easily removed and replaced.

The discharge pipework shall ensure that there is no leakage of contaminated water or foul air into any building.

C.	The work shall be set out and responsibility assumed for the accuracy of the same, and the Client’s representative shall approve the position of all fittings.  When first setting to any work, consideration must be given to the work of other trades.

D.	Responsibility shall be assumed for leaving all unfinished works in safe conditions during the progress of the works.

All materials & equipment are to be installed and protected in such manner as to be adequately covered against damage and deterioration, and during the execution of the work the open ends of all pipework shall be temporarily plugged off by means of blank ends and compression caps respectively.

E.	Vent pipe roof termination

1.	Discharge stacks shall terminate not less than 300 mm above the roof, 900 mm above and not less than 3000 mm, measured horizontally from any window or air conditioner.

2.	Where the stack passes through floors, ceilings and roofs, the openings are to be perfectly sealed-off by proprietary fittings.  They shall terminate with neoprene aluminium weathering slate, weathering collar; and a balloon grating on 180 bend.

F.	Connection to sanitary fittings

All outlets shall be trapped and provided with accessible and adequate means of removal and cleaning.  The traps shall be designed to be self-cleaning all surfaces and joints are to be smooth.

1.	All traps with outlets for pipes up to and including 50 mm shall have a minimum water seal of 75 mm.

2.	Traps with outlets for pipes of over 50 mm shall have a minimum water seal of 50 mm.

The waste pipes to the various sanitary fittings shall be of the following sizes:

Wash basins		 50 mm diameter

W.C's		110 mm diameter

Shower bath tray	 50 mm diameter

Floor gullies		75 mm diameter

Sink		50 mm diameter

G.	Self siphonage tests

The contractor shall undertake tests for self-siphonage and induced siphonage in branch discharge pipes by fitting each appliance to over flowing and then discharging by removing the plugs and discharging the W.C(s) at the upstream end of the discharge pipe.  All seals are to remain in the traps.

The numbers of sanitary appliances to be discharged for this performance test are enumerated below:

| Type of Use | Number of appliances of each kind on the stack | Number of appliances to be discharged simultaneously |  |  |
| --- | --- | --- | --- | --- |
|  |  | 9 litres WC | Wash basin | Kitchen sink |
| ### Domestic | 1 to 9 24 to 24 | 1 1 | 1 1 | 1 2 |
| ### Congested | 1 to 24 5 to 9 10 to 13 14 to 26 27 to 39 40 to 50 | 1 1 2 2 3 3 | 1 2 2 3 4 5 |  |

H.	Testing and commissioning

1.	All tests requested by Local Municipality or engineer on the entire installation shall be carried out, and all necessary appliance and equipment for this purpose shall be supplied.

2.	Provision shall be made to carry out any test requested at any time during the progress of the works or after their completion.

3.	Whilst phased testing may be carried out (which may or may not have been witnessed) it will be required to demonstrate the watertightness, alignment, and level and cleanliness of the whole installation seven days prior to the installation.

4.	This requirement will be discharged by the applying a full running water test to the whole installation as described below and by the drawing through of a drain profile which will be provided to the required detail.

5.	All tests shall be carried out in the presence of the Client's representative, and seven days notice shall be given readiness to test any section of the installation.  Test Certificates shall be submitted to the person witnessing the test, for their signature of approval, to the effect that the system satisfies the requirements of this Specification.

6.	All sections of works must be pretested to satisfy that the system will pass the required test, prior to carrying out the main test.

7.	The Test Certificate shall be required to be completed for all sections of the installation.

8.	After erection and immediately prior to sealing in, all rainwater, main soil, waste, vent and branch soil, waste pipes, shall be checked throughout for obstructions and finally tested for soundness.

9.	The above ground sanitation and rainwater pipe installation shall be subjected to two air tests, one of 75 mm water gauge for a minimum period of 15 minutes prior to connection of sanitary fittings and building in of pipework, and a second air test on completion of the system with all traps and WC's connected when the test pressure shall be 45 mm water gauge for a minimum period of 15 minutes. Water test according  to AWWA  standards shall be followed.

10.	At start of testing sanitation and Rainwater Pipework shall be checked for alignment and stability; mechanical joints shall be re-torqued where necessary.

11.	Access doors shall be removed, felt washers greased and doors replaced.

12.	The whole system shall be rodded through with an appropriately sized disc type plus the allowance shall also be made for testing to the Local Authority requirements and for carrying out separate and independent tests if required.

13.	The provision shall also be made for obtaining an acceptance test certificate form the Local Authority on completion of the works.  The test for the Local Authority shall be allowed for as an addition to the tests required under this specification.

3.02.	POTABLE COLD WATER SERVICES PIPEWORK

A.	Product handling

1.	All products shall be delivered in manufacturer's original protective packaging. All products shall be inspected at time of delivery for damage and for compliance with Specifications. Any products that are found to be damaged or not in accordance with the Specifications shall immediately be repaired or removed from the site and replaced. Repairs shall not be undertaken before the Engineer's review of Contractor's proposed action.

2.	All products shall be handled and stored as recommended by the manufacturer to prevent damage and deterioration. The Contractor shall supply handling equipment such as lifting beams, reinforced canvas slings, protective padding, struts, cradles, etc., required to handle the products without damaging hardware or linings and coatings.

3.	Products shall be protected against damage and the ambient conditions both during transport, site storage and immediately up to the time products are installed. Precautions shall be taken to protect the product from mechanical damage and the effect of sunlight heat, until the backfilling operations have been completed. All site storage areas shall be shaded.

B.	Installation of pipework

1.	Pipework where running below ground level shall be HDPE pipes.  Pipes inside shaft to roof tanks shall be GSP and from risers to cabinet shall be PPR pipes.  Pipe work insulated and exposed to direct sun radiations shall be provided properly with steel cladding.

2.	All pipe work shall run vertically or at an inclination of 1 to the horizontal to enable the whole system to be drained off either through the system or through a valve discharging externally with an air gap to prevent contamination by backflow. When the pipework is drained down, air is to be allowed into the system to prevent failure or damage to the hot water cylinder. A manual air inlet value shall be fitted to the high point in the system to achieve this.

3.	Where pipes are run in walls, floors, etc., all pipework shall be insulated.

4.	All pipe work shall be erected to present a neat and orderly appearance, arranged parallel to or at right-angles to the structural members of the buildings, giving maximum headroom and shall not obstruct windows or doorways. Pipes shall bend round piers, projections and into recesses forming part of the structural works whether so indicated on the drawings or not. Pipework shall be erected such that there is a minimum clearance of 75 mm to the finished floor level and at least 25 mm to the finished wall faces.

5.	All fittings shall, as far as practicable, be the same size as the tubes and pipes connected to them. Bushed outlets will only be accepted if the required outlet size of a fitting is not of standard manufacturer. Eccentric bushings and square tees shall be used where concentric bushing and pitcher tees might cause air to be trapped in the system. Elsewhere square tees shall be confined to dead-leg branches of domestic hot water supply systems and on cold-water branches to fitting or ranges of fittings.

8.	Elbows shall be used, where practicable, in preference to bends Square elbows will not be permitted.

9.	Pipe work shall follow the contours of walls and shall be graded to ensure venting and draining. The clearance between pipework (or the insulation) and the wall and any other fixtures shall be not less than 20 mm.

10.	Purpose-made sets or springs may be used where it is necessary to deviate from a straight run.

11.	Sets or springs in tubes of 50 mm size and above shall be fire-made and tubes shall remain circular after setting.

11.	Eccentric reducing sockets shall be used where changes of bore are made in runs of nominally horizontal pipework to facilitate air venting and draining.

12.	Tubes shall be reamed after cutting and shall be free from dirt, and other defects and shall be thoroughly cleaned before erection. Open ends left during the progress of work shall be temporally closed with purpose-made metal or plastic plugs or caps, or blank metal flanges.

13.	Where pipe passes through walls, ceilings, shall be provided. Pipe passing through flooring shall be provided with approved type floor and ceiling plates fastened securely to the pipe. The sleeves to be of the same metal as the pipe.

14.	All entry and exit holes to or from a building for pipework services shall be sealed and plugged. For service conditions below 60C the sealant shall be mastic compound, above this temperature it shall be silicon rubber. Where the pipework enters the building through a large hole or duct, a mild steel blanking plate not less than 6 mm thick shall be built into the walls of the hole or duct. The service pipes shall pass through clearance sockets welded to the plate and the space between pipe exterior and socket interior shall be sealed and plugged.

15.	All pipes shall be secured by copper or copper alloy clips or brackets to allow for thermal movement and support at spacings not exceeding 300 mm for copper pipes up to 38 mm diameter and 400 mm for those up to 75 mm diameter.

16.	Pipework of 75 mm size and larger subject to expansion and contraction and hung from supports shall be suspended on swivel hangers unless otherwise agreed.

17.	Hangers for horizontal pipework shall be supported in accordance with the requirements of Section 15412 support, Hangers and Brackets.

18.	Piping that is insulated shall be secured by clips that allow sufficient space behind the back of the pipe for the pipe insulation to be properly installed.

19.	All pipework shall be installed so that the vertical distance between the discharge point and overflow level of the receiving appliance shall not be less than 25 mm for taps and/or fittings up to and including 20 mm and 70 mm for those over 20 mm to prevent contamination as result of backflow of water.

20.	A 15 mm diameter washout pipe, discharging outside the building will be provided at ground floor level to drain the system. The top of the outlet is to be in excess of 70 mm from the ground or receiver.

B.	Storage

1.	All pipework shall be stored on purpose made pipe racks of welded construction and of sufficient strength to support the entire weight of the materials without any noticeable deformation.  The racks shall be such that all pipework is clear of the ground.

2.	Pipework fittings shall be stored within a well-lit container made compartmented racks or shelves.  The fittings shall be separated by means of their type and size and laid out in an orderly manner for ease of identification.

C.	System testing

1.	The Contractor shall ensure that all pipework is watertight to the satisfaction of the Engineer and shall supply all pressure gauges, meters, hoses, pumps and other temporary supports, equipment and manpower necessary for carrying out pressure tests.

2.	The Contractor shall, during testing, check the satisfactory operation of each valve installed under the Contract.

3.	Before filling or pressure testing is started the Contractor shall re-check pipes and valves for cleanliness and shall re-check the operation of valves. The open ends of the pipes shall normally be stopped off by blank flanges or capped ends additionally secured where necessary by temporary struts and wedges.

4.	Potable water system shall be tested with water to 1.5 times the normal system working pressure or 6 bar whichever is greater while uncovered but adequately anchored. The testing shall be carried out in sections if necessary. If a section should fail the test, the Contractor shall trace and repair all leaks and defects and retest the section before any further pipes or section of adjacent pipework are laid.

5.	The system shall be filled with potable water and all air expelled. After the system has been completely filled, the pressure shall be steadily and gradually increased until the test pressure has been reached. if any loss is recorded, repairs shall be made and the test re-run.

6.	Written records of every test clearly identifying the tested system together with time of test and name of testing Engineer in tabulated format shall be submitted for review by the Engineer upon completion of the test.

D.	Flushing and disinfection

1.	Potable water pipelines shall be flushed with potable water after completion of pressure testing and before introducing disinfection.

2.	Liquid chlorine, calcium hypochlorite shall be used for disinfection. Where chlorine is used, it shall be introduced only in conjunction with proper equipment and under the supervision of qualified personnel familiar with the physiological, chemical and physical properties of liquid chlorine and who are suitably trained and equipped for dealing with any emergency which may arise from it's use.

3.	Potable water from a suitable source shall be injected with flow control at a constant and measured rate. The water shall receive a dosage of chlorine fed at a measured rate to ensure chlorine concentration in the water entering the pipe is maintained at a minimum of 50 mg/1. The chlorine residual shall be measured at regular intervals to ensure that the required chlorine concentration is maintained.

4.	During the application of chlorine, valves shall be manipulated to prevent the treatment dosage from flowing back into the line supplying the water. Chlorine application shall continue until the entire pipeline is filled with chlorine solution.

5.	After 24 hours retention, the chlorinated water shall be flushed out with potable water, until the chlorine concentration in the water leaving the pipeline does not exceed 21 mg/L. Chlorine residual determination shall be made to ascertain that the heavily chlorinated water has been removed from the pipeline.

6.	Flushing water shall be discharged only to sites or into conduits. Discharges, which cause damage, create nuisance or health hazard, or interfere with the work of others will not be permitted.

END OF SECTION 15410

| DIVISION – 15 MECHANICAL # SECTION – 15411 | TECHNICAL SPECIFICATION MECHANICAL WORK PLUMBING VALVES |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical specification establishes the type and quality of materials, and the standard of workmanship to be used in the supply and installation of valves.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and installation of valves as specified herein and where referred to on the Drawings.

B.	Coordination:  The contractor shall be responsible for the full coordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	Manufacturers:  Firms regularly engaged in the manufacture of valves whose products have been in satisfactory use in similar applications for not less than 10 years.

B.	Installer:  Firms regularly engaged and qualified in the installation of valves with at least 5 years successful installation experience on projects of a similar nature.

1.04	APPLICABLE CODES AND STANDARDS

A.	The valves and all associated materials shall comply fully with the latest relevant British Standards in all respects.

The following are the most commonly used and relevant British Standards associated with valves and associated materials.  However, the Contractor shall ensure that all applicable British Standards are complied with, whether listed here or not.

BS:   21	-	Specification for Pipe Threads for Tubes and Fittings where Pressure Tight Joints are made on the Threads.

BS: 4504   	-	Specification for Ferrous Flanges and Bolting for Pipes, (Part 1)		Valves and Fittings.

BS: 4504   	-	Specification for Copper Alloy and Composite Flanges.

(Part 2)

BS: 5150   	-	Cast Iron Wedge and Double Disk Gate Valves.

BS: 5151   	-	Cast Iron Gate (Parallel Slide ) Valves.

BS: 5152   	-	Cast Iron Globe and Globe Stop and Check Valves.

BS: 5153  	-	Cast Iron Check Valves.

BS: 5154   	-	Copper Alloy Globe, Globe Stop and Check, Check and Gate Valves.

BS: 5156   	-	Diaphragm Valves.

BS: 6683   	-	Guide to Install and Use of Valve.

1.05	SUB

A.	Draw- refer to Section 15010

B.	Products - submit full manufacturers data for every item.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with Section 15010.

1.07	WARRANTY

A.	Provide 12 month warranty in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	GENERAL

- Bodies of valves and cocks on steel pipework up to and including 50mm size shall be of cast gunmetal or bronze. Approved valves having hot-pressed bodies may be offered as an alternative.  Bodies of valves 65mm size and larger shall be of cast iron.  Castings and pressings shall be of good quality, clean and smooth and free from scale or flaws.

- Holes in covers or in gates for screwed portions of spindles shall have full threads of a length not less than the diameter of the spindle over the thread.  Glands shall be machined to provide a running fit between the spindle and the stuffing box.  Stuffing boxes shall be properly packed or fitted with "O" rings, which may be located in plastic bushes.

- Valves and cocks on steel pipework up to and including 50mm size shall have taper screwed ends, and of 65mm size and above shall have flanged ends to BS 4504 Tables 6/2 or 6/5 for welded type and Table 6/4 for screwed type.

- All screwed valves shall have heavy hexagonal reinforcements at openings, threads of ample length to ensure sound joint and heavy shoulders to prevent over entry of pipes, fittings or adapters.

  - Flanged valves shall have flat-faced flanges conforming to BS 4504.

- All valves and valve components (e.g. seatings, packings, etc.) shall be suitable for the working pressures, operating temperatures and conditions of the fluid handled in the systems in which they will be installed.  All valves shall be hydraulically tested to at least twice the working pressure of the systems in which they will be installed.  Where necessary valves shall have extended spindles to facilitate insulation.  The declared pressure rating of the valve shall be equal to or greater than the maximum test pressure of the system.

- The working pressure for valves is to be based on the total static pressure in the pipework in addition to the operating pressure exerted by the pumps on the system.

- Each valve shall have the manufacturer's name or trade mark, the BS number, the nominal diameters, the nominal pressure rating and body material all identified in the form of stamped or cast body markings.

2.02	ISOLATING VALVES

- Isolating valves up to and including 50mm nominal bore shall be bronze or gunmetal gate valves to BS 5154 with solid wedge discs, non-rising stems, screwed in bonnets, metal hand wheels and screwed ends to BS 21 (ISOR/7).

- Isolating valves for 65mm nominal bore and above shall be cast iron gate valves to BS 5150 with solid wedge discs with bronze trim and seatings, bolted on cast iron bonnets, high grade graphited asbestos packings, rising stems with outside screws and yokes, cast iron handwheels and flanged ends to BS 4504.

- Where shown on the drawings or specified herein, lock shield valves shall have easy-clean shields or enclosures to match the inlet valves. As a minimum requirement, one loose key shall be provided for every 25 No valves of the same spindle size.

2.03	NON-RETURN VALVES

- Non-return valves up to and including 50mm nominal bore shall be of the bronze swing pattern with screwed ends and conforming to the requirements of BS 1400.

- Non-return valves 65mm nominal bore and above shall be of the cast iron swing pattern with bolted access covers, solid discs with bronze trim and seatings all to BS 5153 and flanged ends to BS 4504.  An air cock shall be fitted to the bolted cover for air release purposes.

2.04	DRAIN VALVES

- Drain valves shall be of the bronze straight type glanded pattern complete with brass hose union and malleable iron lever conforming to the requirements of BS 1400.

2.05	AIR COCKS

- Air cocks shall be nickel or chrome plated, of the spoutless pattern anwith screwed thread.  Two loose keys shall be provided for each installation having up to 10 air cocks and one loose key shall be provided for every additional ten air cocks.

2.06	AUTOMATIC AIR VENTS

- Automatic air vents shall be of bronze or gunmetal construction and be suitable for hot water.  Vents shall be designed to eliminate air from the system automatically without passage of water.  The unit shall be of the float operated type screwed connection on the outlet to enable the unit to be piped to a remote drain position.

2.07	HOSE BIBS

- Hose bibs shall be bronze ASTM B62 or red brass ASTM B124, with coupling union elbow replaceable hexagonal disc, hose thread spout, vacuum breaker, chrome plated where exposed.

2.08	PRESSURE RATINGS

- Unless otherwise indicated, use valves suitable for 1616 kPa and 121 degrees C.

2.08	PRESSURE REDUCING VALVES

- Valve shall be provided with by pass arrangement complete with all valves and

pressure gauges as detailed on drawings. Valve shall be selected a way from cavitation range.

# PART 3 EXECUTION

3.01	STORAGE

- All valves shall be stored within a well lit container on purpose made compartmented racks or shelves, constructed in a similar manner to support the entire weight of materials without noticeable deformation.

- The valves shall be separated by means of their type and size and laid out in an orderly manner for ease of identification.

- Valves shall be supplied and stored with purpose made or manufactured plugs to prevent ingress of dirt.

3.02	GENERAL INSTALLATION

- Valves with screwed ends shall have a union installed adjacent to the valve for ease of dismantling.

- Where possible, valves shall be installed with the stem in the vertically upright position.  However, all valves shall be installed in a manner such that they are readily accessible for ease of operation.

- Sufficient clearance shall be allowed for the application of thermal insulation, valve boxes, etc.  and to ensure that full travel of the valve stem can be achieved.

3.03	ISOLATING VALVES

- Separate isolating valves shall be provided at all pipe work service of each plant equipment and on pipe main and submain, except where flow measuring or regulating valves are required and these valves can be used for isolating purposes without affecting their measuring or regulating functions.

3.04	DRAIN VALVES

- Drain valves shall be installed at all system low points  on the dead side of isolating valves and on all items of plant to facilitate emptying down and removal.

- Line sized drain valves shall be installed at the end of each pipework run and at the base of each pipework riser to enable the system to be adequately flushed.

3.05	AIR VENTING DEVICES

- Air venting devices shall be installed at all system high points.

- Automatic air eliminators shall be complete with galvanised mild steel relief pipework, taken to within 1.5 m of the floor level with a gunmetal isolating valve and extended to a position where any discharge will not damage building fabrics, decorations or the like.

END OF SECTION 15411

| DIVISION – 15 MECHANICAL SECTION – 15412 | TECHNICAL SPECIFICATION MECHANICAL WORK PLUMBING SUPPORTS, HANGERS AND BRACKETS |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical Specification establishes the type and quality of materials and the standard of workmanship to be used in the supply and installation of Supports, Hangers and Brackets.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and installation of Supports, Hangers and Brackets as specified herein and where referred to on the Drawings.

B.	Coordination: The Contractor shall be responsible for the full coordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	Manufacturers: Firms regularly engaged in the manufacture of Supports, Hangers and Brackets whose products have been in satisfactory use for a similar application for not less than 10 years.

B.	Installer: Firms regularly engaged and qualified in the installation of pipework systems with at least 5 years successful installation experience on projects of a similar nature.

1.04	APPLICABLE CODES AND STANDARDS

A.	The Supports, Hangers and Brackets and all associated materials and workmanship shall comply with the latest relevant British Standards in all respects.

1.05	SUBMITTALS

A.	Drawings: Refer to Section 15010.

B.	Products: Submit full manufacturers data for every item.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with Section 15010.

1.07	WARRANTY

A.	Provide 12 months warranty in accordance with the contract conditions.

1.08	EXTRA MATERIALS

    - Comply with Section 15010.

# PART 2 PRODUCT

2.01	GENERAL

A.	All supports, hangers and brackets shall be of an approved manufacture as herein and indicated on the drawings.

B.	All steel products used for support systems if not manufactured from malleable cast iron or stainless steel shall be either galvanised or painted with one coat of red oxide paint.

C.	All drop rods shall be galvanised and sized to suit the bracket type and system weight but in no case shall be less than 6 mm diameter.

D.	All materials used for support systems shall be compatible with the material they are supporting. Generally steel pipework shall be supported by cast iron and  steel clips, copper pipework by copper or brass clips and UPVC pipework by brass or PVC clips. Where galvanised steel pipework is used all pipework clips shall be galvanised.

E.	Where brackets are exposed to view they shall be of a chrome plated finish.

F.	Fixings to concrete and masonry shall be of the expanding bolt or wedge anchor type selected in accordance with the manufacturers recommendations and suitable for the imposed loads. Where fixings are to be made close to the outside edge of concrete or masonry structures resin banded fixings shall be used to reduce the risk of fracture.

G.	Brackets for fixing to woodwork or lightweight partitioned walls shall be of the screw on pattern.

H.	Purpose made girder clamps shall be used where any system is supported from steelwork and only with the approval of the Engineer.

# PART 3 EXECUTION

3.01	STORAGE

A.	All continuous lengths of channel angle and screwed rod shall be stored on purpose made pipe racks of welded construction and of sufficient strength to support the entire weight of the material without any noticeable deformation. The racks shall be such that all material is clear of the ground.

B.	All raw metal shall be wire brushed and painted with one coat of red oxide paint prior to storage.

C.	All general support materials shall be stored within a well lit container on purpose made compartmented racks or shelving. The materials shall be separated by means of their type and size and laid out in an orderly manner for ease of identification.

3.02	GENERAL

A.	All systems shall be adequately supported in such a manner as to permit free axial movement due to expansion and contraction. Supports shall be arranged as near as possible to joints and changes in direction.

B.	Vertical rising pipes and ducts particularly in shafts shall be adequately supported at the base to withstand the total weight of the riser. Under no circumstances shall branches from vertical rising pipes be the means of support for the vertical pipework.

C.	Hangers for horizontal systems at high level shall be supported from angle or channel irons suitable for securing to the structure.

D.	Pipework shall be independently supported; double stacking of pipes from the same support will not be permitted.

E.	Adjustable mild steel hangers on steel pipework systems shall be used with swivel joints at the pipe rings and spherical washers at the top of the hanger rods. Pipe rings shall be malleable cast iron or fabricated steel made in halves and secured by bolts or screws. Malleable iron hinged pipe rings may also be used but caliper hooks shall not be permitted. Pipework 65 mm diameter and over shall not be supported using malleable iron brackets. All pipe brackets over 50 mm diameter shall be submitted to the Engineer and approved by the Engineer prior to manufacture.

Where rollers and chairs are required, these shall be preformed and where used singularly they shall have restraining "U" straps or bolts formed over the diameter of the pipe and bolted to the base support of the chair. The "U" straps or bolts shall be fitted to allow movement of the pipe without binding. Continuously threaded "U" bolts will not be permitted.

G.	The spacing of supports shall be determined in accordance with the requirement of manufacturer and complying with the related codes. Operating temperatures shall be considered.

END OF SECTION 15412

| DIVISION – 15 MECHANICAL # SECTION – 15430 | TECHNICAL SPECIFICATION MECHANICAL WORK PLUMBING SPECIALTIES |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical specification establishes the type and quality of materials, and the standard of workmanship to be used in the supply and installation of piping specialties.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and installation of piping specialties as specified herein and where referred to on the Drawings.

B.	Coordination: The Contractor shall be responsible for the full coordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	Manufacturers: Firms regularly engaged in the manufacturer of piping specialties whose products have been in satisfactory use for a similar application for not less than 10 years.

B.	Installer: Firms regularly engaged and qualified in the installation of piping specialties with at least 5 years successful installation experience on projects of a similar nature.

1.04	APPLICABLE CODES AND STANDARDS

A.	The piping specialties and all associated materials shall comply fully with the latest relevant British Standards in all respects.

B.	The following are the most commonly used and relevant British Standards associated with piping specialties and associated materials. However the Contractor shall ensure that all applicable British, International, and Jordanian Construction Specification Standards are complied with whether listed here or not.

BS. 21	          :		Specification for Pipe Threads for Tubes and Fittings where Pressure Tight Joints are made on the Threads.

BS 4504 Part 1 :	Specification for Ferrous Flanges and Bolting for Pipes, Valves and Fittings.

BS 4504 Part 2 :	Specification for Copper Alloy and Composite Flanges.

1.05	SUBMITTALS

A.	Drawings - refer to Section 15010

Products - submit full manufacturers data for every item.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with Section 15010.

1.07	WARRANTY

A.	Provide 12 month warranty in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	PIPE SLEEVES

A.	Pipework sleeves shall be of the same materials as the pipework.

B.	The inside diameter of sleeves shall be such as to allow an 8 mm minimum gap between the finished surface of an insulated pipe and the internal surface of the sleeve. The length of the sleeve shall be limited to prevent the sleeve protruding beyond the finished building surface.  Mastic of an approved type shall be inserted between pipe and sleeve as necessary.

2.02	FLOOR, CEILING AND WALL COVER PLATES

A.	Floor, ceiling and wall plates shall be plastic and selected to suit the pipework size and material with which they are to be used.

2.03	PIPE CLEANOUTS

Shall be the same size as the pipe except that cleanout plugs larger than 4 inches (100 mm) will not be reduced.  Cleanouts in connection with other pipe, where indicated, shall be T-pattern, 90-degree branch drainage fittings with cast-brass screw plugs of the same size as the pipe up to and including 4 inches (100 mm).  Cleanout tee branches with screw plug shall be installed at the foot of soil and waste stacks, at the foot of interior downspouts, on each connection to building storm drain where interior downspouts are indicated, and on each building drain outside the building. Round access covers shall be provided and secured to plugs with securing screw.  Square access covers may be provided with matching frames, anchoring lugs, and cover screws.  Cleanouts in finished walls shall have access covers and frames installed flush with the finished wall.  Heads of fastening screws shall not project above the cover surface. UPVC body and S.S cover .

2.04	FLASHINGS

A.	A sheet-lead flashing shield shall be provided for drains and pipe sleeves with integral clamping devices that penetrate a membrane.  Flashing shield shall be made from sheet lead not lighter than 4 pounds (20 kg/m²), and extend not less than 8 inches (20 cm) from the drain or sleeve in all direction.  Flashing shall be inserted into the clamping device and made watertight.  Lean flashing shields, and roof flanges of lead or copper flashing with integral flange, shall be set over membrane in a solid coat of a bituminous cement and strip-flashed as specified by the manufacturer.  Pipes passing through pitches roofs shall be flashed using lead or copper flashing with an adjustable integral flange of adequate size to extend not less than 8 inches (20 cm) from the pipe in all directions and lapped into the roofing to provide a watertight seal.

2.05	FLOOR DRAINS

A.	Shall generally consist of body, integral seepage pan and adjustable perforated or slotted strainer consisting of grate and threaded collar. A suitable clamping device for attaching flashing or waterproofing membrane to the seepage pan without damaging the flashing of waterproofing membrane shall be provided when required. UPVC body and S.S cover .

2.06	ROOF AND BALCONY DRAINS

Roof and balcony drains shall be plastic body and dome.

. Rain water outlets shall be selected to suit the type of roof where installed and shall be provided with a no hub outlet for mechanical jointing to rain water pipe. Rain water outlets shall be provided with perforated extension assemblies, where required to match the roof construction.

2.07  MANHOLES AND GULLY TRAP

- All covers shall be cast iron.

- All manhole covers and frames shall comply with BS EN 124.

- All internal manhole covers shall be bolt down air tight double seal recessed type, they shall be Concrete ring filled with surface finish to match surrounding floor.

- External Manholes:

Covers in paved areas shall be medium duty, double seal, and recessed type. They shall be ring concrete/pavement filled with surface finish to match surrounding floor. Covers subject to vehicular traffic shall be marked heavy duty, single seal, non-rock with square push fit seal plate complete with lifting key-holes.

END OF SECTION 15430

| DIVISION – 15 MECHANICAL SECTION – 15440 | TECHNICAL SPECIFICATION MECHANICAL WORK PLUMBING FIXTURES |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical specification establishes the quality of materials and workmanship to be used in the supply and installation of plumbing fixtures.

1.02	WORK INCLUDED

A.	Provision of all labour, materials and the performance of all operations in connection with the supply and installation of plumbing fixtures as specified herein and shown on the drawings.

B.	Coordination: The Contractor shall be responsible for proper coordination of the work of all trades.

C.	Note for actual specification of type of appliances in toilet areas refer to Section 10800 toilet and bath accessories.

1.03	QUALITY ASSURANCE

A.	Manufacturers: Firms regularly engaged in the manufacture of plumbing equipment and fittings whose products have been in satisfactory use in similar service for not less than 10 years.

B.	Installer: Firms regularly engaged in the installation of plumbing works of a similar quality and scope as this project for at least 5 years.

1.04	APPLICABLE CODES AND STANDARDS

A.	The plumbing fixtures shall comply fully with the latest relevant British and International Standards in all respects.

1.05	SUBMITTALS

A.	Drawings - refer to Section 15010

B.	Products - submit full manufacturer data for every item.

1.06	OPERATION MAINTENANCE DATA

A.	Comply with Section 15010.

1.07	WARRANTY

A.	Provide 12 month warranty in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	GENERAL

- All units and assemblies of sanitary ware shall be as shown on drawings and listed in schedules.

- For selection refer to BOQ and mechanical drawings.

2.02	FITTINGS

A.	Each plumbing fixture shall be installed complete with all necessary fittings for operational and maintenance requirements.

B.	Each water connection to each plumbing fixture shall have a stop valve. The stop valves shall be the same size as the connection and shall be of the wall fixing angle pattern, complete with a chromium plated copper pipe tail for connection to the fixture.

PART 3 EXECUTION

3.01	STORAGE

A.	All plumbing fixtures shall be stored in their original containers in a secure enclosed store. Vitreous china ware shall be stored out of direct sunlight. Fittings (Taps, Showers etc.) shall stored in boxes or wrappings to prevent the ingress of dust to machined surfaces. All storage areas shall have adequate artificial lighting to allow for inspection of the equipment by the engineer.

3.02	INSTALLATION OF FIXTURES

A.	All preparation work (provision of holes, pipes etc.) shall be carried out in strict accordance with the fixture manufacturers requirements and shall be arranged such that pipe fittings, offsets & connections are kept to a minimum. All plumbing fixtures shall be securely fixed to the structure or their support system and shall be plumb & level. The fixtures & their plumbing connections shall be arranged to ensure the connections are not subject to any strain or load from the fixtures.

3.03	INSTALLATION OF FITTINGS

A.	All fittings shall be installed true & straight or where curved, shall follow the manufacturers recommendations to produce a smooth, fair & continuous radius. Any fittings exhibiting  `tool working' or surface finish damage shall be replaced. When positioning fixtures & fittings the contractor shall ensure that all items are central, or where in a range, consistent and symmetrical about architectural finishes as indicated on the drawings.

B.	Where fittings are concealed the contractor shall ensure that they are accessible for maintenance without affecting the structure or finishes.

3.05	PROTECTION

A.	The Contractor shall take all measures necessary to protect fixtures and  fittings during construction. Any damaged fixtures and fittings shall be replaced by  new equivalent units. Repairing of damaged units shall not be accepted.

All fixtures and fittings shall be finally cleaned and put into working order upon completion of construction. The Contractor shall be fully responsible for maintaining these items until the facility is finally handed over.

3.06	TOOLS

A.	The contractor shall supply any special wrenches or other devices necessary for servicing and maintaining the fixtures & fittings. The contractor shall supply 1 No. device for each 10 No. units installed.

END OF SECTION 15440

| DIVISION – 15 MECHANICAL SECTION – 15443 | TECHNICAL SPECIFICATION MECHANICAL WORK SOLAR FLAT PLATE COLLECTORS |
| --- | --- |

- PART 1 GENERAL

  - SUMMARY

- Section includes solar collectors, controls, pipe and fittings, valves, tanks, pumps, cabinet fans, cleaning and chemical treatment of systems.

  - REFERENCES

    - ASME Section VIII - Boiler and Pressure Vessel Code - Pressure Vessels.

    - ASTM International:

      - ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

      - ASTM D635 - Standard Test Method for Rate of Burning [and] [or] Extent and Time of Burning of Plastics in a Horizontal Position.

      - ASTM D1785 - Standard Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120.

      - ASTM D1929 - Standard Test Method for Determining Ignition Temperature of Plastics.

      - ASTM D2241 - Standard Specification for Poly (Vinyl Chloride) (PVC) Pressure-Rated Pipe (SDR Series).

      - ASTM D2310 - Standard Classification for Machine-Made "Fiberglass" (Glass-Fiber-Reinforced Thermosetting-Resin) Pipe.

      - ASTM D2843 - Standard Test Method for Density of Smoke from the Burning or Decomposition of Plastics.

      - ASTM D3309 - Standard Specification for Polybutylene (PB) Plastic Hot- and Cold-Water Distribution Systems.

      - ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

      - ASTM F845 - Standard Specification for Plastic Insert Fittings for Polybutylene (PB) Tubing.

    - American Water Works Association:

      - AWWA C105 - American National Standard for Polyethylene Encasement for Ductile-Iron Pipe Systems.

    - National Fire Protection Association:

      - NFPA 255 - Standard Method of Test of Surface Burning Characteristics of Building Materials.

      - Equivalent EU, DIN standards.

  - Shop Drawings: Indicate manufactured assembly’s system and control schematics, solar collector installation, layout, weights, mounting and support details, and piping connections.

  - Product Data: Submit data on specialties, including manufacturers catalog information. Indicate chemical treatment materials, chemicals, and equipment. Submit certified pump performance and NPSH curve. Submit performance ratings and rough-in details for solar collectors.

    - Manufacturer's Installation Instructions: Submit mounting and other structural requirements.

    - Manufacturer's Certificate: Certify products meet or exceed specified requirements.

    - Manufacturer's Field-Reports: Indicate start-up of treatment systems and include analysis of system water after cleaning and treatment.

  - CLOSEOUT SUBMITTALS

    - Operation and Maintenance Data: Spare parts lists, procedures, and treatment programs.

  - QUALITY ASSURANCE

    - Perform Work in accordance with  MOPWH standard.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years [documented] experience .

    - Installer: Company specializing in performing Work of this section with minimum three years [documented] experience

  - PRE-INSTALLATION MEETINGS

    - Convene minimum one week prior to commencing work of this section.

  - DELIVERY, STORAGE, AND HANDLING

    - Accept and store solar collectors and valves in shipping containers and maintain in place until installation.

    - Protect piping from debris and other foreign matter by using caps on piping connections.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

  - WARRANTY

    - Furnish 12 months manufacturer warranty for collectors.

- PRODUCTS

  - SOLAR COLLECTORS

    - Construction: Unit consisting of assembly of frame, cover, back cover with insulation, absorber plate assembly, and accessories.

    - Frame:

      - Aluminum: Extrusion shapes including I-beam, top battens, double battens, strips, channels, or angles, assembled with stainless steel screws with self sealing neoprene washers.

    - Cover: Low Iron high with selective material absorber.

      - Solar energy transmittance:  minimum 77 percent at 0 degree angle of incidence.

      - Light transmittance: minimum  84  percent.

      - Nominal size: 2000 x 1000 mm.

    - Back Cover: Galvanized steel Plywood with 2 inch (50 mm) thick rigid fiberglass insulation.

    - Plate and Tube Assembly: Copper sheet bonded to copper tubes.

      - Tubes: 0.375 diameter, 0.013 inch (0.016 mm) wall, copper.

      - Sheet: 0.0032 to 0.0035 inch (0.081 to 0.089 mm) thick copper alloy sheet.

      - Working pressure: 150 psig (1034 kPa).

      - Paint: Selective-absorptivity 0.94, emissivity 0.47.

      - Construction: Tubes brazed to header, sheet soldered to tubes.

      - Headers: 0.75 inch (20 mm),1.0 inch (25 mm) Type M copper tube.

      - Sheet width: [22] [34] [44] inches ([560] [860] [1120] mm).

  - DIFFERENTIAL CONTROLLERS

      - Furnish materials in accordance with MOPWH standards.

      - Description: Solid-state differential temperature thermostat with two low resistance thermistors and SPDT relay contactor, and field adjustable differential.

      - Functions:

  - Standard: When collector outlet temperature exceeds storage temperature, close contacts.

  - Ambient Override: When collector temperature is less than  (26 degrees C), open contacts.

  - Freeze prevention circulation: When collector temperature drops below (5.5 degrees C), close contacts and open at (11 degrees C).

  - High Limit Off: When storage temperature rises above  (71 degrees C), open contacts.

  - THERMOSTATS

    - Furnish materials in accordance with MOPWH standards.

    - Electric Thermostat: Low voltage type

    - Line Voltage Thermostats: Integral manual On/Off/Auto selector switch, maximum dead band of (one degree C) concealed temperature adjustment, and locking cover, rated for  load, single or two pole as required.

  - PIPING

    - Copper Tubing: ASTM B88, Type M hard drawn. Or BSEN equivalent

      - Fittings: Cast brass or wrought copper.

      - Joints: Grade 95TA solder joint.

  - GATE VALVES

    - Furnish materials in accordance with MOPHW standards.

    - Up to  (50 mm): Bronze body, bronze trim.

    - Over  (50 mm): Iron body, bronze trim.

  - GLOBE VALVES

    - Furnish materials in accordance with MOPWH standards.

    - Up to  (50 mm): Bronze body, bronze trim.

    - Over  (50 mm): Iron body, bronze trim.

  - BALL VALVES

    - Furnish materials in accordance with MOPWH standards.

    - Up to  (50 mm): Bronze or stainless steel one piece body, stainless steel ball, teflon seat.

    - Over  (50 mm): Cast-steel body, chrome plated steel ball, Teflon seat and stuffing box seals, lever handle, flanged.

  - SWING CHECK VALVES

    - Furnish materials in accordance with MOPWH standards.

    - Up to  (50 mm): Bronze swing disc, solder or screwed ends.

    - Over (50 mm): Iron body, bronze trim, swing disc, renewable disc and seat, flanged ends.

  - RELIEF VALVES

    - Furnish materials in accordance with MOPWH standards.

    - Bronze body, Teflon seat, stainless steel stem and springs, automatic, direct pressure actuated capacities ASME certified and labeled.

  - DIAPHRAGM TYPE COMPRESSION TANKS

    - Furnish materials in accordance with MOPWH standards.

    - Construction: Welded steel, tested and stamped in accordance with ASME Section VIII; rated for working pressure of 125 psig (860 kPa), with flexible diaphragm sealed into tank, and steel legs or saddles.

    - Automatic Cold Water Fill Assembly: Pressure reducing valve, reduced pressure double check back flow preventer, test cocks, strainer, vacuum breaker, and by-pass with valves.

    - Size: As Per schedule

  - AIR VENTS

    - Furnish materials in accordance with  MOPWH standards.

    - Float Type: Brass or semi-steel body, copper float, stainless steel valve and valve seat; suitable for system operating temperature and pressure; with isolating valve.

  - STRAINERS

    - Furnish materials in accordance with MOPWH standards.

    - Size (50 mm) and Under: Screwed brass or iron body for (1200 kPa) working pressure, Y pattern with  (0.8 mm) stainless steel perforated screen.

    - Size (65 mm) to (100 mm): Flanged iron body for (1200 kPa) working pressure, Y pattern with (1.2 mm) stainless steel perforated screen.

    - Size (125 mm) and Larger: Flanged iron body for (1200 kPa) working pressure, basket pattern with (3.2 mm) stainless steel perforated screen.

  - CONTROL VALVES

    - Furnish materials in accordance with  MOPWH standards.

    - Angle or straight pattern, rising stem, globe valve for (860 kPa) working pressure, with bronze body and integral union for screwed connections, renewable composition disc, general purpose solenoid enclosure with continuous duty coil.

  - PUMPS

    - Furnish materials in accordance with MOPWH standards.

    - General Construction Requirements:

      - Balance: Rotating parts, statically and dynamically.

      - Construction: To permit servicing without breaking piping or motor connections.

      - Motors: Operate at 1450 rpm unless specified otherwise.

      - Connections: Flanged.

    - In-Line Circulators:

      - Type: Horizontal shaft, single stage, direct connected to multiple speed motor for in-line mounting,water lubricated, for (860 kPa) maximum working pressure.

      - Construction: Stainless steel housing impeller .

    - Close Coupled Pumps:

      - Type: Horizontal Vertical shaft, single stage, close coupled, radial split casing, for 125 psig (860 kPa) maximum working pressure.

      - Construction: Cast iron casing with suction and discharge gage ports, renewable bronze casing wearing rings, seal flush connection, drain plug, flanged suction and discharge, bronze, fully enclosed impeller keyed to motor shaft extension, mechanical packed seal.

    - Performance:

      - Flow Capacity : As per Schedule

  - CHEMICAL TREATMENT

    - Furnish materials in accordance with MOPWH standards.

    - System Cleaner: Liquid alkaline compound with emulsifying agents and detergents.

    - Closed System Treatment (Water):

      - Sequestering agent to reduce deposits and adjust pH.

      - Corrosion inhibitors.

      - Conductivity enhancers.

    - Anti Freeze solution.

  - ELECTRICAL CHARACTERISTICS AND COMPONENTS

    - Disconnect Switch: Factory mount on equipment control.

- EXECUTION

  - PREPARATION

    - Ream pipe and tube ends. Remove burrs. Bevel plain end ferrous pipe.

    - Remove scale and dirt on inside and outside before assembly.

    - Prepare piping connections to equipment with flanges or unions.

    - After completion, fill, clean, and treat systems.

  - INSTALLATION

    - Install Work in accordance with MOPWH standards and manufacturers recommendations.

    - Route piping in orderly manner, installing plumb and parallel to building structure, and maintain gradient.

    - Install piping to conserve building space, and not interfere with use of space and other work. Group piping whenever practical at common elevations.

    - Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

    - Maintain clearance for installation of insulation, and access to valves and fittings.

    - Install access doors where valves and fittings are not expose

    - Slope piping and arrange systems to drain at low points. Use eccentric reducers to maintain top of pipe level.

    - Where pipe support members are welded to structural building framing, scrape, brush clean, and apply one coat of zinc rich primer to welding.

    - Prepare pipe, fittings, supports, and accessories for finish painting.

    - Install valves with stems upright or horizontal.

    - Support tanks inside building from building structure.

    - Install drain with valve and hose connection on strainer blow down connection.

    - Select system relief valve capacity greater than make-up pressure reducing valve capacity. Select equipment relief valve capacity to exceed rating of connected equipment. Pipe relief valve outlet to nearest floor drain.

    - Verify pumps operate at specified system fluid temperatures without vapor binding and cavitation, are non-overloading in parallel or individual operation, and operate within 25 percent of midpoint of published maximum efficiency curve.

    - Make changes in piping size with reducing fittings. Support piping adjacent to pump so no weight is carried on pump casings.

    - Install line sized shut-off valve and strainer on pump suction, and line sized check valve and balancing valve on pump discharge. Install air vent and drain connection on horizontal pump casings.

    - Install unions downstream of valves and at equipment or apparatus connections.

  - CLEANING

    - After completion, fill, start, and vent prior to cleaning. Use water meter to record capacity in each system. Place terminal control valves in open position during cleaning.

    - Add cleaner to closed systems at concentration as recommended by manufacturer.

    - Circulate for 48 hours, then drain systems as quickly as possible. Refill with clean water, circulate for 24 hours, then drain. Refill with clean water and repeat until system cleaner is removed.

    - Use neutralizer agents on recommendation of system cleaner supplier and acceptance of Architect/Engineer.

    - Flush open systems with clean water for one-hour minimum. Drain completely and refill.

    - Remove, clean, and provide new strainer screens. Inspect, remove sludge, and flush low points with clean water after cleaning process is completed.

    - Closed System Treatment:

      - Install one bypass feeder on each system. Install isolating and drain valves and interconnecting piping. Install around globe valve downstream of circulating pumps [as indicated on Drawings].

      - Introduce closed system treatment through bypass feeder.

  - SCHEDULES

    - See Drawings

END OF SECTION 15443

| DIVISION – 15 MECHANICAL SECTION – 15440 | TECHNICAL SPECIFICATION MECHANICAL WORK PACKAGED BOOSTER PUMP SET |
| --- | --- |

PART 1 - GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes packaged booster pumps to maintain pressure in the building domestic water piping systems:

      - Constant-speed drive packaged booster pumps.

      - Variable-speed-drive, packaged booster pumps.

      - Flexible connectors.

      - Building-automation-system interface.

    - Related Sections include the following:

      - Division 15 Section "Domestic Water Pumps" for domestic water circulation pumps.

  - SUBMITTALS

    - Product Data: For each packaged booster pump specified. Include certified performance curves with operating points plotted on curves; and rated capacities of selected models, furnished specialties, and accessories.

    - Shop Drawings: For packaged booster pumps and accessories. Include plans, elevations, sections, details, and attachments to other work.

      - For installed products indicated to comply with design loads, include structural analysis data

signed and sealed by the qualified engineer responsible for their preparation.

      - Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails and equipment mounting frames.

      - Wiring Diagrams:  Detail power, signal, and control wiring.

    - Operation and Maintenance Data: For each packaged booster pump to include in emergency, operation, and maintenance manuals.

  - QUALITY ASSURANCE

    - Product Options: Drawings indicate size, profiles, and dimensional requirements of packaged booster pumps and are based on the specific system indicated.

    - Electrical Components, Devices, and Accessories: Listed and labeled as defined  in  NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - Packaged booster pumps shall be listed and labeled as pumping systems by testing agency acceptable to authorities having jurisdiction.

  - DELIVERY, STORAGE, AND HANDLING

    - Retain shipping flange protective covers and protective coatings during storage.

    - Protect bearings and couplings against damage.

    - Comply with pump manufacturer's written rigging instructions for handling.

  - COORDINATION

    - Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases. Concrete, reinforcement, and formwork requirements are specified in Division 3.

  - EXTRA MATERIAL

    - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

      - Mechanical Seals: One mechanical seal for each pump.

  - WARRANTY

    - General Warranty: the special warranty specified in this Article shall not deprive the Owner of other rights to Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by the Contractor under requirements of the Contract Documents.

    - Special Warranty: A written warranty, signed by Contractor and manufacturer, agreeing to replace any water distribution pumping station or component that do not meet requirements or that fail within the specified warranty period.

      - Warranty Period: 12 month from the date handing over certificate.

PART 2 - PRODUCTS

  - VARIABLE-SPEED-DRIVE, PACKAGED  BOOSTER PUMPS

    - Description: Multiplex packaged unit, with pumps, piping, valves, sensors, controls, and adjustable- speed-drive units for variable-speed operation.

      - Pressure Rating:  Minimum 1200 kPa (175 psig), and as required to suit system pressure.

      - Pump Arrangement:  Multiple equal-size pumps or as indicated on the schedule of equipment.

    - Pumps: Pumps shall be vertical multistage short-coupled /end suction pumps. (This part applied for all fire and domestic water pump in the project)

      - Impellers:  SAE 40 cast bronze, mixed flow enclosed type.

      - Balancing of Impellers:  Each impeller shall be statically and dynamically balanced prior to assembly in pump casing.

      - Pump shaft:  Stainless steel type 416.

      - Lubrication: Water lubricated type pump.

      - Pump Bowls:  Cast Iron, flanged and bolted.

      - Pump Bearings:  SAE 660 bronze, radial type.

      - Pump Head:  Fabricated steel with continuous bypass for low seal pressure. Cast iron heads are not acceptable. Pump head shall be lined same as pump barrel.

      - Seal: Mechanical general purpose type, with sleeve mounting. Seal shall be rated at 1200 kPa (175 psi) maximum.

      - Adjustable Spacer Coupling: Removable type required so that pump seal can be replaced without disturbing motor.

      - Motor: Comply with requirements in Division 15 Section "Motors. Solid shaft  motors balanced to .22 mm (0.0085-inch) vibration amplitude shall be operated at any point on the pump head curve without overloading the motor. Conform to NEMA 250-Type 2.

      - Pump Barrel: Schedule 40 steel pipe with two-coat "baked" internal lining to meet the potable water requirements of U.S. Food and Drug Administration. Unlined pump barrels are not acceptable.  Provide drain tapping.

    - Variable Frequency (where required):

Controllers:

      - Description: NEMA ICS 2 or DIN equivalent IGBT, Pulse Width Modulation (PWM) type, Microprocessor Controlled Design, IP55 enclosure; listed and labeled as a complete unit and arranged to provide variable speed of an NEMA MG 1 or DIN equivalent Design B, 3-phase induction motor for each pump by adjusting output voltage and frequency.

      - Output Rating: 3-phase; 6 to 50 Hz, with voltage proportional to frequency throughout voltage range.

      - Unit Operating Requirements:

        - Input ac voltage tolerance of 380 to 500 V, plus or minus 10 percent.

        - Input frequency tolerance of 50 Hz, plus or minus 6 percent.

        - Minimum Efficiency:  96 percent at 50 Hz, full load.

        - Minimum Displacement Primary-Side Power Factor:  96 percent.

        - Overload Capability:  1.1 times the base load current for 60 seconds; 2.0 times the base load current for 3 seconds.

        - Starting Torque:  100 percent of rated torque or as indicated.

        - Speed Regulation: Plus or minus 1 percent.

      - Isolated control interface to allow controller to follow control signal over an 11:1 speed range.

      - Internal Adjustability Capabilities:

        - Minimum Speed:  5 to 25 percent of maximum rpm.

        - Maximum Speed:  80 to 100 percent of maximum rpm.

        - Acceleration:  2 to a minimum of 22 seconds.

        - Deceleration:  2 to a minimum of 22 seconds.

        - Current Limit: 50 to a minimum of 110 percent of maximum rating.

      - Self-Protection and Reliability Features:

        - Input transient protection by means of surge suppressors.

        - Undervoltage   and   overvoltage   trips;   inverter   overtemperature,   overload,   and overcurrent trips.

        - Adjustable motor overload relays capable of NEMA ICS 2, Class 20 or DIN equivalent  performance.

        - Notch filter to prevent operation of the controller-motor-load combination at a natural frequency of the combination.

        - Instantaneous line-to-line and line-to-ground overcurrent trips.

        - Loss-of-phase protection.

        - Reverse-phase protection.

        - Short-circuit protection.

        - Motor overtemperature fault.

      - Automatic Reset/Restart: Attempts three restarts after controller fault or on return of power after an interruption and before shutting down for manual reset or fault correction. Bidirectional autospeed search shall be capable of starting into rotating loads spinning in either direction and returning motor to set speed in proper direction, without damage to controller, motor, or load.

      - Power-Interruption Protection: To prevent motor from re-energizing after a power interruption until motor has stopped.

      - Torque Boost: Automatically varies starting and continuous torque to at least 1.5 times the

minimum torque to ensure high-starting torque and increased torque at slow speeds.

      - Motor Temperature Compensation at Slow Speeds: Adjustable current fall-back based on output frequency for temperature protection of self-cooled, fan-ventilated motors at slow speeds.

      - Door-mounted LED status lights shall indicate the following conditions:

        - Power on.

        - Run.

        - Overvoltage.

        - Line fault.

        - Overcurrent.

        - External fault.

      - Panel-Mounted Operator Station:  Start-stop and auto-manual selector switches with manual- speed-control potentiometer and elapsed time meter.

      - Meters or digital readout devices and selector switch, mounted flush in controller door and connected to indicate the following controller parameters:

        - Output frequency (Hertz).

        - Motor speed (rpm).

        - Motor status (running, stop, fault).

        - Motor current (amperes).

        - Motor torque (percent).

        - Fault or alarming status (code).

        - Proportional-integral-derivative (PID) feedback signal (percent).

        - DC-link voltage (volts direct current).

        - Set-point frequency (Hertz).

        - Motor output voltage (volts).

      - Control Signal Interface:

        - Electric Input Signal Interface:  A minimum of 2 analog inputs (0 to 10 V or 0/4-20 mA) and 6 programmable digital inputs.

        - Remote signal inputs capable of accepting any of the following speed-setting input

signals from the control system:

          - 0 to 10-V dc.

2)	0-20 or 4-20 mA.

- Potentiometer using up/down digital inputs.

- Fixed frequencies using digital inputs.                                          5)	RS485.

6)	Keypad display for local hand operation.

        - Output signal interface with a minimum of 1 analog output signal (0/4-20 mA), which can be programmed to any of the following:

          - Output frequency (Hertz).

          - Output current (load).

          - DC-link voltage (volts direct current).

          - Motor torque (percent).

          - Motor speed (rpm).

          - Set-point frequency (Hertz).

        - Remote indication interface with a minimum of 2 dry circuit relay outputs (120-V ac, 1 A) for remote indication of the following:

          - Motor running.

          - Set-point speed reached.

          - Fault and warning indication (over temperature or overcurrent).

          - High- or low-speed limits reached.

      - Communications: RS485 interface allows VFC to be used with an external system within a multi drop LAN configuration. Interface shall allow all parameter settings of VFC to be programmed via BMS control. Provide capability for VFC to retain these settings within the nonvolatile memory.

      - Integral Disconnecting Means: NEMA KS 1, fusible switch with lockable handle.

      - Accessories:

        - Devices shall be factory installed in controller enclosure unless otherwise indicated.

        - Push-Button Stations, Pilot Lights, and Selector Switches: NEMA ICS 2, heavy-duty type or DIN equivalent type .

        - Standard Displays:

          - Output frequency (Hertz).

          - Set-point frequency (Hertz).

          - Motor current (amperes).

          - DC-link voltage (volts direct current).

          - Motor torque (percent).

          - Motor speed (rpm).

          - Motor output voltage (volts).

        - Historical pegging information and displays

        - Cement sensing, phase failure relays for bypass controller.

      - Automatic AFD Bypass

        - Variable speed pumping system shall be equipped with an automatic bypass.

        - Bypass shall consist of a main power disconnect with ground fault protection, a pair of interlocked contactors and a motor overload relay.

        - Automatic bypass shall operate as described in the sequence of operation.

      - Sensor / Transmitters

        - Provide 2 field mounted point pressure sensor transmitter(s) in remote points in the system, as indicated. Units shall transmit an isolated 4-20 mA DC signal indicative of process variable to the pump controller via standard two wire 24 VCD system. Units shall have stainless steel wetted parts with one 0.25” male NPT process connection. It shall be protected against radio frequency interference and shall have a watertight. Accuracy shall be within 0.25% of full span.

      - Sequence of Operation

        - The system shall consist of a pump controller, multiple pump/AFD (as indicated in schedule) sets with manual and automatic alternation and pump staging with across the line bypass for each pump.

        - The pumping system shall start upon the closure of customer’s contact when the pump controller Mode of Operation selector switch is in the REMOTE position.

        - Sensor/transmitters shall be provided as indicated on the plans.

        - Each sensor/transmitter shall send a 4-20mA signal to the pump controller, indicative

of process variable condition.

        - The pump controller shall compare each signal to the independent, engineer/user determined set points.

        - When all set points are satisfied by the process variable, the pump speed shall remain constant at the optimum energy consumption level.

        - The pump controller shall continuously scan and compare each process variable to its individual set point and control to the least satisfied zone

        - PUMP, AFD, OVERLOAD fault shall be continuously scrolled through the display on the operator interface of pump controller until the fault has been corrected and the controller has been manually reset.

        - If the set point cannot be satisfied by the designated lead pump, the pump controller

shall initiate a timed sequence of events to stage a lag pump.

        - The lag pump shall accelerate resulting in the lead pump(s) decelerating until they equalize in speed.

        - Further change in process variable shall cause the pumps to change speed together.

        - When the set point criteria can be safely satisfied with fewer pumps, the pump controller shall initiate a timed destage sequence and continue variable speed operation.

        - As the worst case zone deviates from set point, the pump controller shall send the appropriate analog signal to the AFD to speed up or slow down the pump/motor.

        - The operation of the pumps in the failure mode shall be started through the pump controller and an across the line bypass.

        - When in the "AUTOMATIC" mode, the pump(s) shall operate through the AFD(s)

being controlled by a signal generated by the pump controller.

        - In the event of a system differential pressure failure, due to a pump, AFD, overload fault, the pump controller shall automatically initiate a timed sequence of events to start the remaining pump/AFD set(s) in the variable speed mode. A message on the display shall indicate the fault, pump/motor, or AFD. Subsequent failures shall initiate a timed sequence of events to the variable speed mode as available.

        - In the event of all AFD faults, all pumps shall be automatically started across the line.

        - When in the "BYPASS" mode, the selected pump(s) shall be able to be operated across the line at constant speed with motor overload protection. A solid red light shall signal this condition. All pumps shall be locked out of the variable speed mode.

        - In the event of an overload fault while in the "BYPASS" mode, the selected pump shall

be locked out.

        - In the event of the failure of a zone sensor/transmitter, its process variable signal shall be removed from the scan/compare program. Alternative  zone  sensor/transmitters, shall remain in the scan/compare program for control.

        - The zone number corresponding to the failed sensor/transmitter shall be displayed on the operator interface of the pump controller.

        - In the event of failure to receive all zone process variable signals, the AFD shall maintain 100% speed, reset shall be automatic upon correction of the zone failure.

K.   Manufacturer's Preparation for Shipping:  Clean flanges and exposed machined metal surfaces and treat with anticorrosion compound after assembling and testing. Protect flanges, pipe openings, and pump nozzles.

  - FLEXIBLE CONNECTORS

    - Description: Corrugated, bronze inner tubing covered with bronze wire braid. Include copper-tube ends or bronze flanged ends, braze-welded to tubing. Include 175-psig (1200-kPa) minimum working-pressure rating and ends according to the following:

      - NPS  2  (DN 50)  and  Smaller:  Threaded.  Provide  flanged  ends  if  pump  has  flanged connections.

      - NPS 2-1/2 (DN 65) and Larger:  Flanged.

PART 3 - EXECUTION

  - EXAMINATION

    - Examine roughing-in for packaged booster pumps to verify actual locations of connections before booster pump installation.

  - CONCRETE BASES

    - Install concrete bases of dimensions indicated for packaged booster pumps.

  - BOOSTER PUMP INSTALLATION

    - Install packaged booster pumps level on concrete bases with access for periodic maintenance including removal of pumps, motors, impellers, couplings, and accessories.

    - Support connected domestic water piping so weight of piping is not supported by packaged booster pumps.

  - CONNECTIONS

    - Piping installation requirements are specified in other Division 15 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

    - Connect domestic water piping to packaged booster pumps.  Install suction and discharge pipe equal to or greater than size of unit suction and discharge headers piping.

      - Install flexible connectors on piping connections to unit suction and discharge headers.  Install flexible connectors same size as piping.

      - Install shutoff valves on  piping connections to each  booster pump suction and discharge headers. Install ball, butterfly, or gate valves same size as suction and discharge headers. General-duty valves are specified in Division 15 Section "Valves."

      - Install  union  or  flanged  connections  on  pump  suction  and  discharge  headers  piping  at connection to domestic water piping.

      - Install piping adjacent to packaged booster pumps to allow service and maintenance.

  - STARTUP SERVICE

    - Engage a factory-authorized service representative to perform the following startup service:

      - Complete installation and startup checks according to manufacturer's written instructions.

      - Check piping connections for tightness.

      - Clean strainers if any.

      - Verify that pump controls are correct for required application.

    - Perform the following startup checks for each pump of packaged booster pump unit before starting:

      - Verify bearing lubrication.

      - Prime pumps by opening suction valves and closing discharge valves, and prepare pumps for operation.

      - Start motors.

      - Open discharge valves slowly.

      - Adjust settings.

  - LABELING AND IDENTIFICATION

    - Install  identifying  equipment  makers  and  equipment  signs  on  booster  pumps. Labeling  and identification materials are specified in Division 15 Section "Mechanical Identification."

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain packaged booster pumps.

END OF SECTION 15440

| DIVISION – 15 MECHANICAL SECTION – 15452 | TECHNICAL SPECIFICATION MECHANICAL WORK TANKS |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	The work described in this section covers the support, installation and quality of materials and workmanship for the potable water storage tank installation.

1.02	QUALITY AS

A.	Material and equipment shall be standard products of a manufacturer regularly engaged in the manufacture of products that have been in satisfactory use for a period of ten years.

B.	Installer firms proposed for the installation of the storage tanks and equipment shall have been engaged for at least 5 years in the installation of tanks of a similar type, quality and scope as is required for this project.

1.03	WORK INCLUDED

A.	Provision of all labour, materials, and the performance of all operations necessary for the supply and installation of potable water storage tank and equipment of the as specified herein and as detailed on the Drawings.

B.	Coordination:  The Contractor shall ensure that the storage tanks are fully compatible with all trades, particularly those of the Civil, Mechanical and Electrical services, for successful installation and operation.

C.	Submittals: The Contractor shall submit to the Engineer for review and approval, all calculations and drawings for the equipment proposed and associated builders works to show that the plant as installed will meet all the specified criteria.

No works shall commence on the production of the package or associated site works until the design has received the approval of the Engineer.

1.04 	APPLICABLE CODES AND STANDARDS

# BS 3792:	Installation of Liquid Level and Temperature – Measuring Instruments.

PART 2 PRODUCTS

2.01	GENERAL

A. Cold water storage tanks shall be manufactured to British Standards and to comply strictly with the local codes and Regulations.

B. The tanks shall be provided to the capacities, dimensions and locations shown on the drawings.

D. The Contractor shall submit full specification of the tanks and procedural methods of installation including plans and drawings.

E. The tank shall be manufactured from galvanized steel metal sheets with a minimum thickness of 2mm.

F. Stiffeners tube with a diameter not less than 25mm manufactured from galvanized steel tubes shall be installed in the tank.

G. Each tank is to be fixed on a base, which will support the whole of the tank. The details of the tank base are to be approved to the Engineer approval before any installation work begins.

H. Each tank shall be fitted with the following:

• Ball valve with stopcock

• Overflow pipe on size larger than the ball valve.

• Drain valve provided at the bottom of the tank

• Close fitting openings in cover for water heater vents.

• Manhole cover adjacent to ball valve.

• Air vents with gooseneck and wire mesh.

I. After installation, tanks shall be filled with water for testing for 24 hours. No leakage shall be observed at joints.

J. Tanks shall be guaranteed for minimum 2 years.

PART 3 EXECUTION

3.01	INSTALLATION OF TANKS

A.	Storage tanks to be installed in strict accordance with recommendations.

3.02	INSPECTION OF TANKS AND TESTING

A.	Storage tanks: slowly fill with water to top water level and visually inspect for leaks.

END OF SECTION 15452

| DIVISION – 15 MECHANICAL # SECTION – 15471 | TECHNICAL SPECIFICATION MECHANICAL WORK POTABLE WATER TREATMENT AND FILTRATION EQUIPMENT |
| --- | --- |

PART 1 - GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions apply to this Section.

  - SUMMARY

    - This Section includes the following types of potable water treatment systems and equipment to remove sediment and suspended matter from water:

      - Reverse osmosis.

  - SUBMITTALS

    - Product Data:  For each type of product indicated.

    - Shop Drawings: Detail water filtration equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

      - Wiring Diagrams:  Power, signal, and control wiring.

    - Certificates of Shop Inspections and Data Reports:  For products required to have ASME label, signed by product manufacturer.

    - Operation and Maintenance Data: For water filtration equipment to include in emergency, operation, and maintenance manuals.

  - QUALITY ASSURANCE

    - Source Limitations: Obtain each type of water filtration equipment through one source from a single manufacturer.

    - Electrical Components, Devices, and  Accessories:  Listed  and  labeled  as  defined in  NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - Comply with local codes and requirements for potable water .

  - COORDINATION

    - Coordinate size and location of concrete bases with Architectural and Structural Drawings.

  - EXTRA MATERIALS

    - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

      - Cartridge-Filter Elements:   Elements for cartridge filters equal to 200 percent of amount installed for each size and media indicated.

  - WARRANTY

A.	Provide 12 months warranty in from the date of handing over certificate accordance with the contract conditions.

PART 2 - PRODUCTS

  - Reverse osmosis (light commercial - (5 stages, 600 GPD))

    - Materials: Polypropylene

      - Scope: 10 micron sediment filter, Carbon filter (2nd and 3rd stages), RO membrane, final carbon filter

      - Design Basis:

Unit to have flow regulator on discharge

line to maintain flow.

  - SOURCE QUALITY CONTROL

    - Hydrostatically test before shipment to minimum of one and one-half times pressure rating.

    - Prepare test reports.

PART 3 - EXECUTION

  - EXAMINATION

    - Examine  areas  and  conditions,  with  Installer  present,  for  compliance  with  requirements  for installation tolerances and other conditions affecting performance of filters and separators.

    - Examine roughing-in for piping systems to verify actual locations of piping connections before equipment installation.

    - Examine walls and floors for suitable conditions where filters and separators will be installed.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - CARTRIDGE-FILTER INSTALLATION

    - Install cartridge filters level and plumb, according to layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

    - Install freestanding cartridge filters on concrete bases.

      - Exception:  Omit concrete bases if installation directly on floor is indicated.

    - Attach  wall  brackets  for  off-floor,  wall-mounting,  cartridge  filter  to  vertical  surface.  Attach housing(s), and base if any, to wall bracket.

    - Install housings for off-floor, in-line, cartridge filters in piping.

    - Install filter elements in cartridges.

  - FIELD QUALITY CONTROL

    - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust field-assembled components and equipment installation, including connections, and to assist in field testing.  Report results in writing.

    - Perform the following field tests and inspections and prepare test reports:

      - Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

      - Operational Test:  After electrical circuitry has been energized, start units to confirm proper unit operation.

      - Test and adjust controls and safeties.   Replace damaged and malfunctioning controls and equipment.

    - Water Quality Test: Perform Laboratory micro biological test and chemical analysis of the potable water to record the performance of the equipment, and provide a certificate that the quality of potable water is in compliance with local codes and approved by authority having jurisdiction.

    - Remove and replace water filtration equipment that does not pass tests and inspections and retest as specified above.

  - STARTUP SERVICE

    - Engage a factory-authorized service representative to perform startup service for water filtration and treatment equipment.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain water filtration and treatment equipment.

END OF SECTION 15471

| DIVISION – 15 MECHANICAL # SECTION – 15487 | TECHNICAL SPECIFICATION MECHANICAL WORK ## DOMESTIC HOT WATER STORAGE HEATERS (CALORIFIERS) |
| --- | --- |

PART 1 –   GENERAL

1.1	RELATED DOCUMENTS

A. 	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2	SUMMARY

A.	This Section includes the following heat exchangers:

1.	Hot water calorifiers.

.

1.3	SUBMITTALS

A.  	Product Data: For each type and size of heat exchanger indicated.  Include rated capacities, operating characteristics, furnished specialties, and accessories.

B.	Shop Drawings: Diagram power, signal, and control wiring.

C.	Product Certificates: For each type of circulating heat exchanger, signed by product manufacturer.

D.	Manufacturer Seismic Qualification Certification:  Submit certification that heat exchangers, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls," Include the following:

E.	Operation and Maintenance Data:  For heat exchangers to include in emergency, operation, and maintenance manuals.

1.4	QUALITY ASSURANCE

A.  	Source Limitations:  Obtain same type of heat exchangers through one source from a single manufacturer.

B.  	Product Options: Drawings indicate size, profiles, and dimensional requirements of heat exchangers and are based on the specific system indicated.

C. 	Electrical  Components,  Devices,  and  Accessories:  Listed  and  labeled  as  defined  in  NFPA 70, Article 100 or European/British Standards, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. 	ASME Compliance: Where ASME-code construction is indicated, fabricate and label heat-exchanger storage tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1 or European/British Standards.

E.  	Comply with NSF 61 (or European/British Compliance), "Drinking Water System Components - Health Effects; Sections 1 through 9" for all components that will be in contact with water.

1.5	COORDINATION

A.	Coordinate size and location of concrete bases with Architectural and Structural Drawings.

1.6	WARRANTY

A. 	Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of heat exchangers that fail in materials or workmanship within specified warranty period.

1.	Failures include, but are not limited to, the following:

a.	Structural failures including heat exchanger, storage tank, and supports.

b.	Faulty operation of controls.

c. 	Deterioration of metals, metal finishes, and other materials beyond normal use.

2.	Warranty Period(s):  From date handing over certificate:

a.	Storage Heat Exchangers: 12 months.

PART 2 –  PRODUCTS

2.1	HOT WATER CALORIFIERS

A. 	Description: Packaged, double coil hot-water storage tank with heat-exchanger coil; controls; and specialties for heating domestic water with heating hot water in coil.

B. 	Flow Pattern: Standard-flow arrangement, with water from bottom of storage tank circulated across heat-exchanger coils and returned to tank. Include hot-water outlet located at top of tank and temperature sensor in tank.

C.  	Storage Tank Construction: ASME code or BSEN , steel or corrosion-resistant metal with 12 bars working-pressure rating. Include nozzle and head for heat-exchanger tube coil.

1.	Configuration:  Vertical or Horizontal.

2.	Tapping: Factory fabricated of materials compatible with tank. Attach tapping to tank before testing and labeling.

- NPS 2 (DN 50) and Smaller: Threaded ends.

- NPS 2-1/2 (DN 65) and Larger: Flanged ends.

3.	Insulation: Fiberglass, Polyurethane, or manufacturer’s standard that is suitable for operating temperature. Surround entire storage tank and nozzle except connections and controls.

4.	Jacket: Steel, with baked enamel finish, or manufacturer’s standard.

5.	The tank shall have all necessary tapings, including tap for aqua stat, standard manhole, and steel supports. Tank shall be glass lined or as per manufacturer recommendation. The liner shall resist the corrosive action of water and shall not change the color, taste or odor and effectively prevent rust being generated in the tank.

D.	Heat-Exchanger Coil: copper or copper-alloy, U tubes with tube sheet and supporting baffles.

1.	Heat-Exchanger Pressure Rating: Equal to or greater than heating-fluid supply pressure.

E.	Temperature Control: Adjustable thermostat.

F. 	Safety Control: Automatic, high-temperature-limit cutoff device or system. Include automatic low- water cutoff device or system.

G. 	Relief Valves: ASME rated and stamped and complying with ASME PTC 25.3 or European/British Standards, for combination temperature and pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than working-pressure rating of heat exchanger. Select one relief valve with sensing element that extends into storage tank.

H.	Gages:  Factory-mounted thermometer and pressure gage.

I.	Miscellaneous Components for Heating Hot-Water Units: Control valve, valves, and piping.

J.	Support: Factory mounted on skids.

2.2	HEAT-EXCHANGER ACCESSORIES

A.	Combination Temperature and Pressure Relief Valves: ASME rated and stamped and complying with ASME PTC 25.3 or European/British Standards.   Include relieving capacity at least as great as heat input, and include pressure setting less than working-pressure rating of heat exchanger.  Select relief valves with sensing element that extends into heat-exchanger storage tank.

2.3	SOURCE QUALITY CONTROL

A.	Test and inspect heat-exchanger storage tanks, specified to be ASME-code construction, according to ASME Boiler and Pressure Vessel Code or European/British Standards.

B.	Prepare test reports.

PART 3 -  EXECUTION

3.1	HEAT-EXCHANGER INSTALLATION

A.	Install heat exchangers on concrete bases.

B. 	Install  heat  exchangers  level  and  plumb,  according  to  layout  drawings,  original  design,  and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

C.	Anchor heat exchangers to substrate.

D. 	Install temperature and pressure relief valves in top portion of storage tank shells of heat exchangers with domestic water storage.  Use relief valves with sensing elements that extend into shells.

Extend relief-valve outlet, with drain piping same as water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

E.  	Install heat-exchanger drain piping as indirect waste to spill by positive air gap into open drains or over floor drains.  Install hose-end drain valves at low points in water piping for heat exchangers that do not have tank drains.   Refer to Division 15 Section "Plumbing Specialties" for hose-end drain valves.

F. 	Install  thermometer  on  each  heat-exchanger  domestic-water inlet  and  outlet  piping,  and  install thermometer  on  each heat-exchanger heating-fluid inlet and outlet piping.

G. 	Install pressure gages on heat-exchanger heating-fluid piping.

H.	Fill heat exchangers with water.

I.	Charge compression tanks with air.

3.2	CONNECTIONS

A.  	Piping installation requirements are specified in other Division 15 Sections.    Drawings indicate general arrangement of piping, fittings, and specialties.

B.  	Install piping adjacent to heat exchangers to allow service and maintenance.  Arrange piping for easy removal of heat exchangers.

3.3	FIELD QUALITY CONTROL

A. 	Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust field-assembled components and equipment installation, including connections.  Report results in writing.

B.	Perform the following field tests and inspections and prepare test reports:

1.	Leak Test:  After installation, test for leaks.  Repair leaks and retest until no leaks exist.

2.	Operational Test:  After electrical circuitry has been energized, confirm proper operation.

3.	Test and adjust controls and safeties.   Replace damaged and malfunctioning controls and equipment.

3.4	DEMONSTRATION

A. 	Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain heat exchangers.

END OF SECTION 15487

| DIVISION – 15 MECHANICAL SECTION – 15500 | TECHNICAL SPECIFICATION MECHANICAL WORK HEATING, VENTILATION AND AIR CONDITIONING |
| --- | --- |

PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	HVAC scope

B.	Basis of design

C.	Systems descriptions

1.02	HVAC SCOPE

A.	The Heating, Ventilation and Air Conditioning shall include the following systems and all systems and components shown of the drawings.

a)	HVAC.

b)	Ventilation systems.

- Toilet and kitchen mechanical ventilation.

1.03	BASIS OF DESIGN

##### A.	DESIGN CRITERIA USED FOR HVAC CALCULATIONS

1.	External ambient

Summer	:	39C dry bulb, 20.3C wet bulb (for coil selections)

Daily Range: 11C

Otherwise indicated on the drawings

###### Winter	:	0C dry bulb

###### Site location	: Jordan

Altitude	:	700 m above sea level

Latitude	:	32 N

The above summer design temperature does not apply to equipment operating ambients, which are given separately in this specification

2.	Internal Conditions

- Inside design conditions

Refer to drawings

# PART 2 PRODUCTS

Not used

# PART 3 EXECUTION

Not used

END OF SECTION 15500

| DIVISION – 15 MECHANICAL # SECTION – 15513 | TECHNICAL SPECIFICATION MECHANICAL WORK ## HVAC NOISE CONTROL |
| --- | --- |

# PART 1	 GENERAL

## 1.01	SCOPE OF SECTION

### A.	This technical specification details the noise control requirements for the HVAC equipment, plant and systems.

## 1.02	WORK INCLUDED

### A.	The work includes the provision of all labour material and the performance of all operations in connection with the supply and installation of HVAC noise control equipment.

## 1.03	APPLICABLE CODES AND  STANDARD

The testing of all noise control equipment and the methods used in measuring the noise ratings of air conditioning  plant and equipment shall be in accordance with the relevant sections of the following British and International  standards, unless otherwise stated:-

BS 4718:1971	Methods of Test of silencers for Air Distribution Systems.

BS 2750:

Parts 1-9-1980	Laboratory and Field Measurement of Airborne Sound Insulation of Various Building Elements.

Recommendations for Field and Laboratory Measurement of Airborne  and  Impact Sound Transmission in Buildings.

BS 3638:1987	Method of Measurement of Sound Adsorption in a Reverberation Room.

BS 4773:

Part 2:1976	Acoustic Testing.

BS 4856;

Part 4:1978	Acoustic performance without Additional Ducting of Forced Fan Convection Equipment.

Part 5:19	Acoustic Performance with Additional Ducting of Forced Fan Convection Equipment.

BS 4857:

Part 2:1978(1983)	Acoustic Testing and Rating of High Pressure Terminal Reheat Units.

BS 4954:

Part 2:1978(1987)	Acoustic Testing and Rating of Induction Units.

BS 5643:1984	Glossary Refrigeration, Heating, Ventilating  and Air Conditioning  Terms.

## 1.04	SUBMITTALS

### A.	Drawings - refer to 15010

### B.	Calculations - manufacturers selection calculations justifying equipment proposed for specified parameters.

### C.	Product - full certified manufacturers data for each type of product.

## 1.05	OPERATION AND MAINTENANCE DATA

### A.	Comply with 15010

## 1.06	WARRANTY

### A.	Provide 12 months warranty in accordance with contract conditions.

# PART 2 PRODUCTS

## 2.01	ANTI-VIBRATION MOUNTINGS

### A.	All items of rotating and reciprocating plant and equipment shall be isolated  from the structure by the use of anti-vibration materials, mountings or spring loaded supports fixed to either concrete bases, inertia  blocks or support steels as indicated.

### B. 	Centrifugal fans and motors within package units shall be isolated from the frame of the unit by suitable anti-vibration mountings. Fan discharge air connection shall be fitted with approved flexible connections internally isolating the fan scroll from the air-handling unit casing.

### C. 	Axial flow fans shall mounted on steel legs on diaphragm plates supported on neoprene in shear anti-vibration mountings, or suspended using spring loaded hangers to suit the application.

### G. 	The contractor shall take great care in ensuring that the package unit manufacturer selects the correct anti-vibration mounting to suit the deflections of the structural steelwork at Roof level. Initial guidance is given in the schedules but the contractor shall make full submissions to the Engineer confirming equipment weights, a.v. mount details and configurations prior to placing the equipment on order.

### H. 	The construction of the anti-vibration mountings shall generally comply with the following: -

1.	Enclosed spring mountings (caged or restrained springs)

Each mounting shall consist of cast or fabricated telescopic top and bottom housings enclosing one or more helical steel springs as the principal isolation elements, and shall incorporate a built-in levelling device.

The springs shall have an outside diameter of not less than 75% of the operating height, and be selected to have at least 50% overload capacity before becoming coil-bound.

The bottom plate of each mounting shall have bonded to it a neoprene pad designed to attenuate any high frequency energy transmitted by the springs.

Mountings incorporating snubbers or restraining devices shall be designed so that the snubbing damping or restraining mechanism is capable of being adjusted to have no significant effect during the normal running of the isolated machine.

2.	Open spring mountings

Each mounting shall consist of one or more helical steel springs as the principal isolation elements, and shall incorporate a built-in levelling device.  The springs shall be fixed or otherwise securely located to cast or fabricated top and bottom plates, and shall have an outside diameter of not less than 75% of the operating height, and shall be selected to have at least 50% overload capacity before becoming coil-bound.

The bottom plate shall have bonded to it a neoprene pad designed to attenuate any high frequency energy transmitted by the springs.

3.	Neoprene-in-shear mountings

Each mounting shall consist of a steel top plate and base plat completely embedded in oil resistant neoprene.  Each mounting shall be capable of being fitted with a levelling device, and bolt holes in the base plate and tapped holes in the top plate so that they may be bolted to the floor and equipment where required.

## 2.02	FLEXIBLE CONNECTIONS

### A. 	Flexible connections shall be provided on all ductwork connections to fans, rotating plant and equipment isolated from structure on anti-vibration materials or mountings. Ductwork crossing building movement construction joints shall be installed with flexible connections.

### B. 	Flexible connections on ductwork to fans shall be a minimum/maximum free length of 100mm./200mm. respectively to minimise noise transmission and noise breakout. They shall be complete free from stress and shall not be required to accept any weight.

### C. 	Thicknesses and strengths of flexible connection materials shall be suitable to withstand the positive and negative fan pressures to which they will be subjected to and shall not allow perceptible leakage. The materials shall be durable, non-flammable having good acoustical quality.

### F. 	Flexible connections shall allow freedom of movement of plant in all planes.

# PART 3 EXECUTION

### A. 	All moving plant, machinery and apparatus shall be statically and dynamically balanced at manufacturers works and certificates issued.

### B.	Moving plant, machinery and apparatus including line equipment shall be isolated from the building structure.

### C. 	Electrical conduits and connections to all moving plant and equipment shall be carried out in flexible conduit and cables to prevent the transmission of vibration to the structure and nullify the provisions of anti-vibration mountings.

### D. 	All duct connections to fans shall incorporate flexible connections, except in cases where these are fitted integral within air handling units.

### E. 	Ductwork connections to the fan inlets/outlets shall be concentrically aligned so that the flexible connections are not subjected to any strain and not used as a means of correcting bad misalignment.

### F. 	All resilient acoustic-absorbing materials shall be non-flammable, vermin and rot proof and shall not tend to break up or compress sufficiently to transmit vibration or noise from the equipment to the structure.

END OF SECTION 15513

| DIVISION – 15 MECHANICAL SECTION – 15856 | TECHNICAL SPECIFICATION MECHANICAL WORK AIR MOVERS: CENTRIFUGAL AND AXIAL |
| --- | --- |

# PART 1 GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following:

      - Backward-inclined centrifugal fans.

      - Propeller fans,

      - Circular inline axial smoke rated fans

  - PERFORMANCE REQUIREMENTS

    - Project Altitude:  Base fan performance ratings on actual Project site elevations above sea level.

    - Operating Limits:  Classify according to AMCA 99.

  - REFERENCES

    - All Fans shall comply fully with the latest edition of the British and International standards.

    - BS 848 – Fans for general purposes.

    - BS 4675 – Mechanical vibration in rotating machinery.

    - BS 5060 – Specification for performance and construction of electric circulating fans and regulators.

    - BS  5285  –  Specification.  Performance  of  a.c.  electric  ventilating  fans  and  regulators  for  non- industrial use.

    - BS 6339 – Specification for dimensions of circular flanges for general purpose industrial fans.

    - BS EN 25136 – Acoustics. Determination of sound power radiated into a duct by fans. In-duct method.

    - ABMA 9 - Load Ratings and Fatigue Life for Ball Bearings.

    - ABMA 11 - Load Ratings and Fatigue Life for Roller Bearings.

    - AMCA 99 - Standards Handbook.

    - AMCA 204 - Balance Quality and Vibration Levels for Fans.

    - AMCA 210 - Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

    - AMCA 300 - Reverberant Room Method for Sound Testing of Fans.

    - AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data.

    - ARI 1060 - Air-to-Air Energy Recovery Ventilation Equipment Certification Equipment Program.

    - NEMA MG 1 - Motors and Generators.

    - NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

    - UL 705 - Power Ventilators.

  - SUBMITTALS

    - Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated and include the following:

      - Certified fan performance curves with system operating conditions indicated.

      - Certified fan sound-power ratings.

      - Motor ratings and electrical characteristics, plus motor and electrical accessories.

      - Material thickness and finishes, including color charts.

      - Dampers, including housings, linkages, and operators.

    - Shop  Drawings:  Detail  equipment  assemblies and indicate dimensions,  weights, loads,  required clearances, method of field assembly, components, and location and size of each field connection.

      - Wiring Diagrams:  Power, signal, and control wiring.

      - Design  Calculations:  Calculate requirements  for  selecting vibration  isolators and seismic restraints and for designing vibration isolation bases.

      - Vibration Isolation Base Details: Detail fabrication, including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails, and base weights.

    - Coordination Drawings: Show fan room layout and relationships between components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate and certify field measurements.

    - Field quality-control test reports.

    - Operation and Maintenance Data:  For  centrifugal  fans to include in  emergency,  operation,  and maintenance manuals.

    - Selection data for each fan for approval prior to ordering.

  - QUALITY ASSURANCE

    - Electrical Components, Devices, and Accessories: Listed  and  labeled  as  defined  in  NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - AMCA Compliance:  Products shall comply with AMCA performance requirements as follow:

      - Sound-Power Level Ratings: Tested according to AMCA 300.

      - Fan Performance Ratings: Tested and rated according to AMCA 210.

    - NEMA Compliance:  Motors and electrical accessories shall comply with NEMA 1or DIN equivalent  .

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver  fans  as  factory-assembled  units,  to  the  extent  allowable  by  shipping  limitations,  with protective crating and covering.

    - Disassemble  and  reassemble  units,  as  required  for  moving  to  the  final  location,  according  to manufacturer's written instructions.

    - Lift and support units with manufacturer's designated lifting or supporting points.

  - COORDINATION

    - Coordinate size and location of structural-steel support members.

    - Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.

  - EXTRA MATERIALS

    - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

      - Belts:  One set for each belt-driven unit.

  - WARRANTY

    - General Warranty: the special warranty specified in this Article shall not deprive the Owner of other rights  the Owner may have under other provisions of the Contract Documents and shall be in addition to and run concurrent with, other warranties made by the Contractor under requirements of the Contract Documents.

    - Special Warranty: A written warranty, signed by Contractor and manufacturer, agreeing to replace any axial fan or component that do not meet requirements or that fail within the specified warranty period.

      - Warranty period: 12 months from date of handing over certificate of the centrifugal fans.

PART 2 - PRODUCTS

  - GENERAL FAN REQUIREMENTS

    - General:

      - Performance data for all fans and spare parts shall be determined in accordance with the

provisions of ASHRAE 51.

      - Sound pressure level ratings of ducted fans shall comply with AMCA 301 and shall be the result of tests made in accordance with AMCA 300.

      - Sound pressure level ratings shall conform to AMCA 302.  Unit construction shall conform to applicable standards contained in AMCA 99 and to requirements specified.

      - Safety provisions for power transmission equipment and non-ducted inlets and outlets shall include guards and screens, unless other provisions are required, and shall be constructed in accordance with applicable provisions of ASME B15.1. Installation shall be such that fan vibration-isolation provisions are not negated.

      - Fan wheels shall be statically and dynamically balanced at the factory.

    - Corrosion Protection: All steel shall be mill-galvanized, or phosphatized and coated with minimum two  coats, corrosion resistant enamel paint. Manufacturers paint and paint system shall meet the minimum  specifications of: ASTM D 1735 water fog; ASTM B 117 salt spray; ASTM D 3359 adhesion; and ASTM G 23 weathermeter.

    - Air-Handling System  Balancing  Provisions:  All  necessary facilities  shall  be  provided  for  the adjustment  of  fan  speed  for  each  air-handling  system  during air-quantity balancing  operations. Facilities provided shall be one of the following:

      - A variable-pitch drive with variable range to produce the fan speed necessary for proper air balance.

      - A continuously variable drive or power unit to produce the fan speed necessary for proper air balance.

      - A series of fixed-pitch pulleys that can be interchanged until the proper fan speed has been determined.

    - Fans used for the smoke extract system shall be fire rated for 300˚C two hours.

  - BACKWARD-INCLINED CENTRIFUGAL FANS

    - Description:  Factory-fabricated,  -assembled,  -tested,  and  -finished,  belt-driven  centrifugal  fans consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, and support structure.

    - Housings: Formed panels to make curved-scroll housings with shaped cutoff; with doors or panels to allow access to internal parts and components.

      - Panel Bracing:  Steel angle- or channel-iron member supports for mounting and supporting fan scroll, wheel, motor, and accessories.

      - Horizontally split, bolted-flange housing.

      - Spun inlet cone with flange.

      - Outlet flange.

    - Backward-Inclined Wheels: Single-width-single-inlet and double-width-double-inlet  construction with  curved inlet flange, back plate, backward-inclined blades welded or riveted  to  flange  and back plate; cast-iron or cast-steel hub riveted to back plate and fastened to shaft with set screws.

    - Shafts:  Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

      - Turned, ground, and polished hot-rolled steel with keyway.  Ship with a protective coating of lubricating oil.

      - Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

    - Prelubricated and Sealed Shaft Bearings: Self-aligning, pillow-block-type ball bearings.

      - Ball-Bearing Rating Life:  ABMA 9, Ll0 at 120,000 hours.

    - Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

      - Service Factor Based on Fan Motor Size:  1.3.

      - Fan Pulleys:   Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

      - Motor Pulleys: Adjustable pitch for use with motors through 5 hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

      - Belts:  Oil resistant, non-sparking, and non-static; matched sets for multiple belt drives.

      - Belt Guards: Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation. Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

      - Motor Mount:  Adjustable for belt tensioning.

    - Accessories:

      - Scroll Access Doors:  Shaped to conform to scroll, with quick-opening latches and gaskets.

      - Cleanout Door:   Bolted gasketed door allowing access to fan scroll, of same material as housing.

      - Scroll Drain Connection:   NPS 1 (DN 25) steel pipe coupling welded to low point of fan scroll.

      - Companion Flanges:  Rolled flanges for duct connections of same material as housing.

      - Variable Inlet Vanes:  With blades supported at both ends with two permanently lubricated bearings of same material as housing. Variable mechanism terminating in single control lever with control shaft for double-width fans.

      - Discharge Dampers: Assembly with opposed blades constructed of two plates formed around and to shaft, channel frame, and sealed ball bearings; with blades linked outside of airstream to single control lever of same material as housing.

      - Inlet Screens:  Grid screen of same material as housing.

      - Shaft Cooler:   Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

      - Spark-Resistant Construction:  AMCA 99.

      - Shaft Seals:  Airtight seals installed around shaft on drive side of single-width fans.

      - Weather Cover:  Enameled-steel sheet with ventilation slots, bolted to housing.

    - Motors:  NEMA MG.1

      - Enclosure Type:  Totally enclosed, fan cooled.

  - PROPELLER FANS

    - Description: belt-driven or direct-drive propeller fans as indicated, consisting of fan blades, hub, housing, orifice ring, motor drive, and accessories.

    - Housings: Galvanized steel sheet with flanged edges and integral orifice ring with baked-enamel finish coat after assembly.

    - Steel Fan Wheels: Formed-steel blades riveted to heavy-gage spider bolted to cast-iron hub.

    - Belt-driven Drive assembly: Resiliently mounted to the housing, statically and dynamically balanced and selected for continuous operation at the maximum rated fan speed and motor horsepower (HP), with final alignment and belt adjustment made after installation.

      - Service Factor Based on Fan Motor: 1.4.

      - Fan Shaft: Turned, ground, and polished steel keyed to wheel hub.

      - Shaft Bearings: permanently lubricated, permanently sealed, self-aligning ball bearings.

        - Ball-Bearing Rated Life: AFBMA 9, L-10 of 100,000 hours.

      - Pulleys: Cast iron with split, tapered bushing, dynamically balanced at factory.

      - Motor Pulleys: Adjustable pitch for use with motors through 5 HP; fixed pitch for use with motors larger than 5 HP. Select pulley so pitch adjustment is at the middle of the adjustment range at fan design conditions.

      - Belts: Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

      - Belt Guards: Fabricate of steel for motors mounted on the outside of the fan cabinet.

    - Accessories: The following accessories are required as indicated:

      - Gravity  Shutters:  Aluminum  blades  in  aluminum  frame,  interlocked  blades  with  nylon bearings.

      - Motor-Side Back Guard: Galvanized steel, conforming to OSHA specifications, removable for maintenance.

      - Wall Sleeve: Galvanized steel to match fan and accessory size.

      - Weathershield Hood: Galvanized steel to match fan and accessory size.

      - Weathershield Front Guard: Galvanized steel with expanded metal screen.

      - Variable-Speed Controller: Solid-State control to reduce speed from 100 percent to less than 50 percent.

      - Disconnect Switch: Nonfusible type, with thermal-overload protection mounted inside fan housing, factory wired through an internal aluminum conduit.

.

  - SOURCE QUALITY CONTROL

    - Sound-Power Level Ratings: Comply with AMCA 301,  "Methods  for  Calculating  Fan  Sound Ratings from Laboratory Test Data." Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans." Label fans with the AMCA-Certified Ratings Seal.

    - Fan Performance Ratings: Establish flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests and ratings according to AMCA 210, "Laboratory Methods of Testing Fans for Rating."

PART 3 - EXECUTION

  - INSTALLATION

    - Install fans level and plumb.

    - Support floor-mounting units using restrained spring isolators having a static deflection of 1 inch (25 mm).

    - Install floor-mounting units on concrete bases designed to withstand, without damage to equipment, the seismic force required by authorities having jurisdiction.

    - Support suspended units from structure using threaded steel rods and spring hangers having a static deflection of 1 inch (25 mm).

    - Install units with clearances for service and maintenance.

    - Label fans according to requirements specified in Division 15 Section "Mechanical Identification."

  - CONNECTIONS

    - Duct installation and connection requirements are specified in other Division 15 Sections. Drawings indicate  general arrangement of ducts and duct  accessories.  Make final  duct  connections with flexible connectors. Flexible connectors are specified in Division 15 Section "Duct Accessories."

    - Install ducts adjacent to fans to allow service and maintenance.

    - Install line-sized piping from scroll drain connection, with trap with seal equal to 1.5 times specified static pressure, to nearest floor drain.

  - FIELD QUALITY CONTROL

    - Perform the following field tests and inspections and prepare test reports:

      - Verify that shipping, blocking, and bracing are removed.

      - Verify that unit is secure on mountings and supporting devices and that connections to ducts and  electrical components are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

      - Verify that cleaning and adjusting are complete.

      - Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation.   Reconnect fan drive system, align and adjust belts, and install belt guards.

      - Adjust belt tension.

      - Adjust damper linkages for proper damper operation.

      - Verify lubrication for bearings and other moving parts.

      - Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

      - Remove and replace malfunctioning units and retest as specified above.

    - Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

  - ADJUSTING

    - Adjust damper linkages for proper damper operation.

    - Adjust belt tension.

    - Lubricate bearings.

  - CLEANING

    - After completing installation, inspect exposed finish.   Remove burrs, dirt, and construction debris, and repair damaged finishes including chips, scratches, and abrasions.

    - Clean fan interiors to remove foreign material and construction debris.  Vacuum clean fan wheel and cabinet.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain fans.

END OF SECTION 15856

| DIVISION – 15 MECHANICAL SECTION – 15890 | TECHNICAL SPECIFICATION MECHANICAL WORK ## DUCTWORK |
| --- | --- |

# PART 1 GENERAL

1.01	SCOPE OF SECTION

A.	This technical Specification establishes the type and quality of materials and the standard of workmanship to be used in the supply and installation of Metal Ductwork.

1.02	WORK INCLUDED

A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and installation of metal ductwork as specified herein and where referred to on the Drawings.

B.	Coordination:  The Contractor shall be responsible for the full coordination of the work of all trades.

1.03	QUALITY ASSURANCE

A.	Manufacturers:  Firms regularly engaged in the factory fabrication of Metal Ductwork whose products have been in satisfactory use in a similar application for not less than 10 years.

B.	Installer:  Firms regularly engaged and qualified in the installation of Metal Ductwork with at least 5 years successful installation experience on projects of a similar nature.

1.04	APPLICABLE CODES ANDSTANDARDS

A.	The Metal Ductwork and all associated materials and workmanship shall comply fully with the latest relevant standards in all respects.

B.	The following are the most commonly used and relevant British, American and other Standards for Metal Ductwork and associated materials. However, the Contractor shall ensure that all applicable standards are complied with whether listed here or not.

1.	Specification for sheet metal ductwork No. DW 143 and Addendum "A" 1988 for low, medium and high pressure / velocity air systems published by heating, ventilating contractors association (HVCA) UK.

2.	The SMACNA (Sheet Metal and Air Conditioning Contractors' National Association, Inc.) duct manual and sheet metal construction for ventilating and air conditioning systems

3.	Low Pressure Duct Construction Standards, 5th ed. (SMACNA).

4.	Rectangular Industrial Duct Construction Standards. (SMACNA)

5.	The ASHRAE handbook published by the American Society of Heating, Refrigerating and Air Conditioning Engineers Inc. - Duct Construction

6.	ASTM Standard A525 : Hot Dipped Galvanized Steel Sheets

7.	Standard for the Installation of Air Conditioning and Ventilating Systems (National Fire Protection Association, ANSI/NFPA 90A-93).

8.	Standard for the Installation of Air Conditioning and Ventilating Systems (National Fire Protection Association, ANSI/NFPA 90A-93).

9.	Standard for the Installation of Warm Air Heating and Air Conditioning Systems (National Fire Protection Association, ANSI/NFPA 90B-93).

1.05	SUBMITTALS

A.	Drawings refer to 15010

B.	Calculations - refer to 15010.

Fan head calculations shall be submitted to the engineer for approval based on Contractor ductwork working drawings.

C.	Products - Typical duct section and fittings to demonstrate integrity of construction.

D.	Full details of air test procedures.

1.06	OPERATION AND MAINTENANCE DATA

A.	Comply with 15010

1.07	WARRANTY

A.	Provide 12 months warranty in accordance with contract conditions.

# PART 2 PRODUCTS

2.01	GENERAL

      - Steel metal duct

A.	All figure numbers referred to throughout this ductwork specification relate to those contained in DW 143 or SMACNA.

B.	 Ductwork for ventilation and air conditioning supply and return shall be galvanized steel G90.

C.	Ductwork shall be manufactured to the sizes detailed on the drawings, however where ductwork is to be internally lined the ductwork size shall be increased to compensate for the lining thickness.

D.	The interior surfaces of all ductwork shall be smooth.  No sheet metal parts, tabs, angles, or similar shall project into the air stream for any reason unless specified to do so.  All seams and joints shall be external.

E.	The minimum nominal sheet thickness for any ductwork shall be 0.7 mm for internal systems with the longer duct size up to 1000mm.  Where the longer duct size exceeds 900 mm the nominal sheet thickness shall be 0.9 mm.

F.	The Contractor shall ensure that the choice of gauge thickness for ductwork and the stiffening provision is such that the ductwork installation does not drum or vibrate. Single stiffeners shall be used as illustrated in figures 44-49 inclusive of DW 143.

G.	All ductwork operating at pressures classified as "High" and "Medium" pressure shall be tested to establish conformity with leakage limits set out in DW 142 and in accordance with procedures described in DW 143.

Additionally samples of straight duct beads and tees on low, medium and high velocity ductwork systems should be selected and pressure tested during erection to demonstrate the adequacy of jointing methods.

H.	All jointing and construction methods shall be approved by the Engineer.

I.	Approved sealant shall be used on all ductwork longitudinal seams.  The sealant can be included in the seam during manufacture and applied as an edge sealant.

J.	Button punch snap lock longitudinal joints shall not be used.

K.	Particular attention shall be given to ensuring that cross jointing methods are suitable for the specified pressure rating.  Cross joints shall generally be flanged and corner treatment shall be such that corners pull-up true and square and do not leak.  An approved liquid or mastic sealant shall be used on all cross joints.

L.	Aerofoil section turning vanes shall be used on all 90 square bends. Turning vanes shall be securely attached at each end either to the duct or to internal runners and the runners fastened to the duct by mechanically-closed rivets or bolts at 150mm maximum spacing.  Turning vanes in twin bends in which the widths of the straight section and branch differ shall be set so that the leading and the trailing edges of the turning vanes are parallel to the duct axis.

M.	Change shapes that maintain the cross sectional area shall have sides where the slope does not exceed 22.5o on any side.  Should it be necessary to reduce the cross sectional area the slope shall not exceed 15o on any side and the reduction in area shall not exceed 20%.  In this instance the approval of the Engineer shall be sought prior to manufacture.

N.	The slope of expansions and contractions shall not exceed 22.5o on any side unless it is unavoidable, in which case splitters shall be provided to bisect the angle between the sloping side and the centre line of the duct.

O.	Ductwork connections to plant and equipment (eg. cooling and heating coils,) shall, in the case of bolted flanges, be provided with matching flanges of similar size and thickness.  Sheet metal returned flanges shall not be permitted.

P.	The ductwork sizes indicated on the drawings are nominal, therefore for socket and spigot joints the actual dimensions of ductwork and fittings shall be correctly related so that when installed the joint shall be effectively sealed.

Q.	Bends shall be either segmented with swaged ends, or in the case of ductwork 400mm diameter and below, pressed bends of the long radiuses type shall be acceptable.

R.	Tapers of the concentric type shall be manufactured with an angle not exceeding 15o.  Tapers of the eccentric type shall have angles not exceeding 30o.

S.	Hangers and supports for ductwork systems shall generally comply with DW 142 Part 6.  Primary fixings into the building structure shall be subject to approval by the Engineer.

T.	Ductwork hangers and supports shall be adjustable for height, spaced to ensure adequate support and where practicable, fitted at each ductwork joint or spaced at not more than the maximum centres in Tables 24, 25 and 26 for rectangular, circular and flat oval horizontal ducting.  Securing of formed brackets to corners of ductwork as a means of suspension shall not be permitted.

U.	Supports for vertical ductwork in buildings shall be generally located at each floor slab but subject to a maximum spacing of 4 metres.

V.	All ductwork shall be securely supported from the building structure but inert packing material shall be provided between ducts and supports to prevent direct contact of the ducting with the structure.

        - Thermal insulators shall be installed between sheet metal ductwork carrying conditioned air and the support steelwork as described in this specification and as shown on the drawings.

- All  outdoor duct work shall be surface treated with proper painting materials to prevent galvanized steel from corrosive ambient

      - SEALANT AND GASKETS

    - General Sealant and Gasket Requirements: Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50.

    - Fire Resistant Sealing Materials.

      - Sealing materials shall be silicone based formulated for use in through-penetration fire- stopping around pipes and duct penetrations through fire-rated walls and floors. Sealants and accessories shall have fire-resistance ratings indicated, as established by testing identical as- semblies in accordance with ASTM E814, by Underwriters' Laboratories, Inc., or other testing and inspection agency acceptable to authorities having jurisdiction.

      - Sealant

        - Provide ready-to-use silicone penetration seal that will stop passage of fire, smoke, and water through fire-rated wall and floor penetrations and will cure in the presence of at- mospheric moisture to produce durable and flexible seal, and will form airtight and wa- tertight bonds with most common building materials in any combination including cement, masonry, steel, and aluminum.

        - Sealant Composition shall be one-part ready-to-use materials with consistency of soft caulk at temperatures ranging from -35 to 160 F, and extension and compression prop- erties of plus/minus 40% of original gap.

      - Foam

Provide "free foam" density, two-part silicone elastomer, supplied in liquid components with easy identification.

      - HANGERS AND SUPPORTS

    - Hanger Rods for Noncorrosive Environments: Electrogalvanized steel rods and nuts.

    - Hanger Rods for Corrosive Environments: Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

    - Strap and Rod Sizes: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible

    - Steel Cables for Galvanized-Steel Ducts: Galvanized steel.

    - Steel Cable End Connections:   Cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

    - Duct Attachments: Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

    - Trapeze and Riser Supports:

      - Supports for Galvanized-Steel Ducts: Galvanized-steel shapes and plates.

      - FLEXIBLE CONNECTORS

    - General: Flexible connectors shall be provided on fan inlet and outlet connections. They shall be of the full cross sectional area of the matching fan inlet or outlet or duct section. The ends of the ducts and for connection shall be in line.

    - Flame retardant or non-combustible fabrics fabricated from chemically impregnated canvas.

    - Conventional indoor system flexible connector: Glass fabric double coated.

    - Conventional outdoor system flexible connector: Glass fabric double coated with weatherproof coating resistant to sun UV rays.

      - FLEXIBLE DUCTWORK

    - General

      - Where flexible connections are indicated or required between rigid ductwork and particular component or items of equipment the internal diameter of the flexible duct shall be equal to the external diameter of the rigid duct. The use of flexible ductwork between rigid sections of sheet metal ductwork to change direction or plane will not be permitted except where indicated.

      - The flexible duct shall  have a  liner  and a  cover  of rough heat-resistant  fabric equal  in durability and flexibility to glass fiber fabric and shall be impregnated and coated with plastic. It shall be reinforced with a bonded galvanized spring steel wire helix between the liner and the cover and an outer helix to glass fiber cord or equal shall be bonded to the cover to ensure regular convolutions. Insulation shall be (38mm) thick, glass fiber.

      - The leakage from any section of flexible air duct shall not exceed 1% of the design air flow rate at the static operating pressure.

      - Flexible ducts shall be suitable for an operating temperature range of -18°C to - 120°C and shall  comply with BS 476 Part 1, Section 2, Clause 7 (class 1: surface of very low flame spread).  Pressure rating (1500pa) positive and (125Pa) negative.

      - Flexible ducts shall be supported at 1m centers.

      - DUCT ACCESS DOORS, PANELS AND SECTIONS

    - Provide access doors, sized and located for maintenance work, upstream, in the following locations:

      - Each duct mounted coil and humidifier.

      - Each fire damper (for link service), smoke damper and automatic control damper.

      - Each duct mounted smoke detector.

      - For cleaning operating room supply air duct and kitchen hood exhaust duct, locate access doors at 6 m (20 feet) intervals and at each change in duct direction.

    - Openings shall be as large as feasible in small ducts, 300 mm by 300 mm (12 inch by 12 inch) minimum where possible. Access sections in insulated ducts shall be double-wall, insulated. Transparent shatterproof covers are preferred for uninsulated ducts.

      - For rectangular ducts: Refer to SMACNA Standards.

      - For round and flat oval duct: Access sections shall be not less than 1.0 mm (20 gage) housing welded or riveted to a duct section.

      - INSTRUMENT TEST FITTINGS

    - Manufactured type with a minimum 50 mm (two inch) length for insulated duct, and a minimum 25 mm (one inch) length for duct not insulated. Test hole shall have a flat gasket for rectangular ducts and a concave gasket for round ducts at the base, and a screw cap to prevent air leakage.

    - Provide instrument test holes at each duct or casing mounted temperature sensor or transmitter, and at entering and leaving side of each heating coil, cooling coil, and heat recovery unit.

# PART 3 EXECUTION

3.01	STORAGE

A.	Ductwork shall be either stored on purpose made racks of welded construction, or in a dry open area stored clear of the ground.

B.	All open ends of ductwork shall be sealed with polythene sheeting to prevent the ingress of dirt.

C.	Small ductwork sections shall not be stored within larger sections except in the case of circular ducts.

D.	Ductwork shall not be stacked in a manner that will result in damage to or deform of the sections will occur.

E.	All ductwork shall be stored with an identification label indicating the piece number, size and location in which it is to be installed.

3.02	FIXINGS

A.	Mechanically closed rivets shall be used strictly in accordance with the manufacturers recommendations with regard to use, size and clearance drill size.

B.	Bolts, nuts and washers shall be used for flanged sections of ductwork and shall be of mild steel protected by electro galvanizing, cadmium plating or a similar approved finish.

C.	Self tapping screws shall be used subject to the approval of the Engineer, in instances where other types of fixing is not practical.

D.	Welding shall not be permitted on galvanized sheet steel materials.

3.03	GENERAL INSTALLATION

    - Drawing plans, schematics, and diagrams indicate general location and arrangement of duct system.

Indicated duct locations, configurations, and arrangements were used to size ducts and calculate friction loss for air-handling equipment sizing and for other design considerations. Install duct systems as indicated unless deviations to layout are approved on Shop Drawings and Coordination Drawings.

    - Install ducts according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" unless otherwise indicated.

    - Install round and flat-oval ducts in maximum practical lengths.

    - Install ducts with fewest possible joints.

    - Install factory- or shop-fabricated fittings for changes in direction, size, and shape and for branch connections.

    - Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

    - Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

    - Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

- Route  ducts  to  avoid  passing  through  transformer  vaults  and  electrical  equipment  rooms  and enclosures.

- Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges of same metal thickness as the duct.  Overlap openings on four sides by at least 1-1/2 inches (38 mm).

- Where  ducts  pass  through  fire-rated  interior  partitions  and  exterior  walls,  install  fire  dampers.

Comply with requirements in Division 15 Section "Duct Accessories" for fire and smoke dampers.

- Protect  duct  interiors  from  moisture,  construction  debris  and dust,  and other  foreign  materials.

Comply with SMACNA's "Duct Cleanliness for New Construction Guidelines."

- Duct cleanliness Level : C (advance level) according to SMACNA

3.04	FIELD QUALITY CONTROL

    - Perform tests and inspections.

    - Leakage Tests:

      - Comply with SMACNA's "HVAC Air Duct Leakage Test Manual."

      - Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

      - Test for leaks before insulation application.

      - Conduct tests at static pressures equal to maximum design pressure of system or section being tested. If static-pressure classes are not indicated, test entire system at maximum system design pressure.  Do not pressurize systems above maximum design operating pressure.

    - Duct System Cleanliness Tests:

      - Visually inspect duct system to ensure that no visible contaminants are present.

    - Duct system will be considered defective if it does not pass tests and inspections.

    - Prepare  test  and  inspection  reports  containing the  quantity of each  inspection  on  the  executed ductworks and its related accessories.

3.05	DUCT CLEANING

    - Clean new and existing duct system(s) before testing, adjusting, balancing.

END OF SECTION 15890

| DIVISION – 15 MECHANICAL SECTION – 15910 | TECHNICAL SPECIFICATION MECHANICAL WORK DUCTWORK ACCESSORIES |
| --- | --- |

PART 1 - GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - Section Includes:

      - Backdraft and pressure relief dampers.

      - Manual volume dampers.

      - Fire dampers.

      - Flange connectors.

      - Turning vanes.

  - REFERENCES

    - The ductwork accessories shall comply fully with the latest relevant British or American standards and codes.

    - The following standards are the most commonly used, however the contractor shall comply with all relevant standards whether listed or not

      - NFPA 90A - Standard for the Installation of Air Conditioning and Ventilating Systems.

      - NFPA 92A - Recommended Practice for Smoke-Control Systems.

      - NFPA 92B - Guide for Smoke Management Systems  in Malls, Atria, and Large Areas

      - SMACNA - HVAC Duct Construction Standard - Metal and Flexible.

      - ASHRAE Standard 90.1-2001- Energy Standard for Buildings except Low-Rise Residential Buildings.

      - UL 33 - Heat Responsive Links for Fire-Protection Service.

      - UL 555 - Fire Dampers.

      - UL 555S - Leakage Rated Dampers for Use in Smoke Control Systems.

      - AMCA500 – Test Method for Louvers, Dampers and shutters.

  - SUBMITTALS

    - Product Data:  For each type of product indicated.

      - For duct silencers, include pressure drop and dynamic insertion loss data.  Include breakout noise calculations for high transmission loss casings.

    - Shop Drawings:  For duct accessories.  Include plans, elevations, sections, details and attachments to other work.

      - Detail duct accessories fabrication and installation in ducts and other construction. Include dimensions, weights, loads, and required clearances; and method of field assembly into duct systems and other construction.  Include the following:

        - Special fittings.

        - Manual volume damper installations.

        - Control damper installations.

        - Fire-damper,  smoke-damper,  combination  fire-  and  smoke-damper,  ceiling,  and

corridor damper installations, including sleeves; and duct-mounted access doors and remote damper operators.

        - Duct security bars.

        - Wiring Diagrams:  For power, signal, and control wiring.

    - Coordination Drawings: Reflected ceiling plans, drawn to scale, on which ceiling-mounted access panels and access doors required for access to duct accessories are shown and coordinated with each other, using input from Installers of the items involved.

    - Source quality-control reports.

    - Operation and Maintenance Data: For air duct accessories to include in operation and maintenance manuals.

  - QUALITY ASSURANCE

    - Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," and with NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

    - Comply with AMCA 500-D testing for damper rating.

    - Comply with applicable codes and requirements of local authorities having jurisdiction whichever is more stringent.

  - EXTRA MATERIALS

    - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

      - Fusible Links: Furnish quantity equal to 10 percent of amount installed.

PART 2 - PRODUCTS

  - MATERIALS

    - Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated. Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

    - Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

      - Galvanized Coating Designation: G90 (Z275).

      - Exposed-Surface Finish:  Mill phosphatized.

    - Aluminum Sheets: Comply with ASTM B 209 (ASTM B 209M), Alloy 3003, Temper H14; with mill finish for concealed ducts and standard, 1-side bright finish for exposed ducts.

    - Extruded Aluminum: Comply with ASTM B 221 (ASTM B 221M), Alloy 6063, Temper T6.

    - Reinforcement Shapes and Plates:  Galvanized-steel reinforcement where installed on galvanized sheet metal ducts; compatible materials for aluminum and stainless-steel ducts.

    - Tie Rods:  Galvanized steel, 1/4-inch (6-mm) minimum diameter for lengths 36 inches (900 mm) or less; 3/8-inch (10-mm) minimum diameter for lengths longer than 36 inches (900 mm).

  - BACKDRAFT AND PRESSURE RELIEF DAMPERS

    - Description:  Gravity balanced, suitable for horizontal or vertical installation.

    - Frame: galvanized sheet steel with welded corners and mounting flange.

    - Blades:  Multiple single-piece blades, center-pivoted, sheet with sealed edges.

    - Blade Action: Parallel.

    - Blade Seals:  Neoprene mechanically locked.

    - Blade Axles: Galvanized steel.

    - Tie Bars and Brackets:  Galvanized steel.

    - Return Spring:  Adjustable tension.

  - MANUAL VOLUME DAMPERS

    - Standard, Manual Volume Dampers: Factory fabricated with required hardware and accessories – Multiple or single blade parallel or opposed blade design as indicated, and suitable for horizontal or vertical applications.

      - Frames:

        - Hat shaped.

        - Galvanized steel channels.

        - Mitered and welded corners.

        - Flanges for attaching to walls and flangeless frames for installing in ducts.

      - Blades:

        - Multiple or single blade.

        - Parallel- or opposed-blade design.

        - Stiffen damper blades for stability.

        - Galvanized, roll-formed steel.

      - Blade Axles:  Galvanized steel.

      - Bearings:

        - Oil-impregnated bronze.

        - Dampers in ducts with pressure classes of 3-inch wg (750 Pa) or less shall have axles full length of damper blades and bearings at both ends of operating shaft.

      - Blade Seals:  Neoprene.

      - Tie Bars and Brackets:  Galvanized steel.

      - Accessories:

        - Include  locking  device  to  hold  single-blade  dampers  in  a  fixed  position  without vibration.

      - Splitter Dampers:

        - Material: Same gage as duct to 600 mm size in both dimensions, and two gages heavier for sizes over 600 mm.

        - Fabricate blades of single thickness sheet metal to streamline shape for low velocity systems and double thickness sheet metal to streamline shape for high velocity air systems. Blades shall be secured with continuous hinge or rod.

        - Operator: Minimum 6 mm diameter rod in self aligning, universal joint action, flanged bushing with set screw.

        - Single Blade Dampers: Fabricate for duct sizes up to 150 mm in height.

      - Quadrants:

        - Furnish locking, indicating quadrant regulators on single and multi-blade dampers.

        - On insulated ducts mount quadrant regulators on standoff mounting brackets, bases, or adapters.

        - Quadrant shall be with lockable cadmium plated screws, nuts and washers.

        - The quadrant shall be clearly marked "open" and "shut".

        - Where rod lengths exceed 750 mm furnish regulator at both ends.

  - FIRE DAMPERS

    - Type:  Static and dynamic; rated and labeled according to UL 555 by an NRTL.

    - Fire rating:

      - Dampers shall have a UL555 fire rating of 1 ½ hours when used for the protection of openings in walls, partitions, or floors with the resistance ratings of less than 3 hours.

      - Dampers shall have a UL555 fire rating of 3 hours when used for the protection of openings in walls, partitions, or floors having a fire resistance rating of less than 3 hours or more.

    - Frame: Curtain type with blades outside airstream except when located behind grille where blades may be inside airstream; fabricated with roll-formed, galvanized steel; with mitered and interlocking corners.

    - Mounting Sleeve:  Factory- or field-installed, galvanized sheet steel.

      - Minimum Thickness:  0.052 or 0.138 inch (1.3 or 3.5 mm) thick, as indicated, and of length to suit application.

    - Mounting Orientation:  Vertical or horizontal as indicated.

    - Blades:  Roll-formed, interlocking, galvanized sheet steel.  In place of interlocking blades, use full- length, galvanized-steel blade connectors.

    - Horizontal Dampers: Include blade lock and stainless-steel closure spring.

    - Heat-Responsive Device:  Fusible link, replaceable, factory installed, 165 deg F (74 deg C) rated.

  - TURNING VANES

    - Manufactured Turning Vanes for Metal Ducts:  Curved blades of galvanized sheet steel; support with bars perpendicular to blades set; set into vane runners suitable for duct mounting.

    - General Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible"; Figures 2-3, "Vanes and Vane Runners," and 2-4, "Vane Support in Elbows."

    - Vane Construction:  Double wall.

PART 3 - EXECUTION

  - INSTALLATION

    - Install duct accessories according to applicable details in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for metal ducts.

    - Install duct accessories of materials suited to duct materials; use galvanized-steel accessories in galvanized-steel and fibrous-glass  ducts,  stainless-steel  accessories  in  stainless-steel  ducts,  and aluminum accessories in aluminum ducts.

    - Install backdraft dampers at inlet of exhaust fans or exhaust ducts as close as possible to exhaust fan unless otherwise indicated.

    - Install volume dampers at points on supply, return, and exhaust systems where branches extend from larger ducts. Where dampers are installed in ducts having duct liner, install dampers with hat channels of same depth as liner, and terminate liner with nosing at hat channel.

    - Set dampers to fully open position before testing, adjusting, and balancing.

    - Install test holes at fan inlets and outlets and elsewhere as indicated.

    - Install fire and smoke dampers according to UL listing, NFPA, safety regulations and as shown on the drawings.

    - Connect ducts to duct silencers with flexible duct connectors.

    - Install  duct  access  doors  on  sides  of ducts to allow for  inspecting,  adjusting,  and maintaining accessories and equipment at the following locations:

  - On both sides of duct coils.

  - Upstream and downstream from duct filters.

  - At drain pans and seals.

  - Downstream  from  manual  volume  dampers,  fire  dampers,  control  dampers,  backdraft dampers, and equipment.

  - Adjacent to and close enough to fire or smoke dampers, to reset or reinstall fusible links.

Access doors for access to fire or smoke dampers having fusible links shall be pressure relief access doors and shall be outward operation for access doors installed upstream from dampers and inward operation for access doors installed downstream from dampers.

  - Upstream and downstream from turning vanes.

  - Control devices requiring inspection.

  - Elsewhere as indicated on drawings and details.

    - Install access doors with swing against duct static pressure.

    - Label  access  doors  according  to  Division 15  Section  "Identification  for  HVAC  Piping  and Equipment" to indicate the purpose of access door.

    - Install flexible connectors to connect ducts to equipment.

    - Install duct test holes where required for testing and balancing purposes.

    - Install fire dampers at all fire compartments to maintain integrity of fire rating.

    - Install duct silencer / sound attenuators wherever required by calculations showing that sound level exceeds the applicable code (ASHRAE requirements).

  - FIELD QUALITY CONTROL

    - Tests and Inspections:

      - Operate dampers to verify full range of movement.

      - Inspect locations of access doors and verify that purpose of access door can be performed.

      - Operate  fire,  smoke,  and  combination  fire  and  smoke  dampers  to  verify  full  range  of movement and verify that proper heat-response device is installed.

      - Inspect turning vanes for proper and secure installation.

      - Operate remote damper operators to verify full range of movement of operator and damper.

  - ADJUSTING

    - Adjust duct accessories for proper settings.

    - Adjust fire and smoke dampers for proper action.

    - Final positioning of manual-volume dampers is specified in Division 15 Section "Testing, Adjusting, and Balancing".

  - DEMONSTRATION

    - Demonstrate  re-setting  of  fire  dampers  to  the  engineer  and  owner’s  representatives.  Time of demonstration shall be coordinated with both the engineer and the owner.

END OF SECTION 15910

| DIVISION – 15 MECHANICAL # SECTION – 15940 | # TECHNICAL SPECIFICATION # MECHANICAL WORK # AIR OUTLETS AND INLETS |
| --- | --- |

# PART 1	GENERAL

## 1.01	SCOPE OF SECTION

### A.	This technical Specification establishes the type and quality of materials and the standard of workmanship to be used in the supply and installation of Air Outlets and Inlets or Air Terminal Devices.

## 1.02	WORK INCLUDED

### A.	The work includes the provision of all labour, materials and the performance of all operations in connection with the supply and installation of air terminal devices as specified herein and where referred to on the Drawings and Schedules.

### B.	Coordination:  The Contractor shall be responsible for the full coordination of the work of all trades.

## 1.03	APPLICABLE CODES AND STANDARDS

### A.	The air terminal devices and all associated materials and workmanship shall comply fully with the latest relevant British Standards and ISO Standards in all res.

### The following are the most commonly used and relevant British Standards and ISO standards associated with air terminal devices and associated materials. However, the Contractor shall ensure that all applicable British Standards and ISO Standards are complied with whether listed here or not.

BS: 4773	:	Methods for testing and rating air terminal devices for air distribution systems: Part 1, Aerodynamic testing.

ISO: 5219	:	Air distribution and air diffusion: Laboratory aerodynamic testing and rating of air  terminal devices.

### B.	Applicable industry definitions - refer to schedules.

### Given below are definitions of the basic terms to describe the characteristics of ATDs.

### Core Area (Ac) The gross area containing all the openings of the ATD.

### Free area (A) This is the sum of the smallest areas of the cross-section of all the openings of an ATD.

### Effective area (Ao) This is the smallest area of an ATD through which air passes and which may not be equal to its free area.  It is given by:

### Ao = Cd A

### where A is the free area and Cd is discharge coefficient which usually varies between 0.65 and 0.9.

### Free area ratio (Ra) This is the ratio of free area to core area.

### Envelope  This is a surface of the jet produced by a supply ATD which has the same velocity, usually taken to be 0.25 or 0.5 m/s

### Throw (Xm) The maximum distance between the plane of a supply ATD and a plane which is tangential to the jet envelope and perpendicular to the initial jet direction.

### Drop or rise (Ym) The vertical distance between the centre of a supply core and a horizontal plane tangential to the envelope.

### Spread (Zm) The maximum horizontal distance between two vertical planes tangento the envelope of a supply ATD and perpendicular to a plane through the core axis.

### Core velocity (Uc) The volume of air flow rate divided by the core area of the ATD.

### Discharge velocity (Uo) The average velocity at the discharge from an opening of an ATD which is equal to Uc/(CdRa).

## 1.04	SUBMITTALS

### A.	Drawings refer to 15010

### B.	Report on works test.

### C.	Manufacturers data for each type of ATD including confirmed noise and performance details.

## 1.05	OPERATION AND MAINTENANCE DATA

### A.	Comply with 15010

## 1.06	WARRANTY

### A.	Provide 12 months warranty in accordance with contract conditions.

# PART 2 PRODUCTS

## 2.01	GRILLES and RIGESTERS

### A.	Grilles shall be of aluminum extrusion of the types and sizes indicated on the drawings and in the schedules and be of the concealed fixing type.  Where the size is not indicated, the grilles shall be selected for the air volume flow rates indicated in the schedules to achieve the required throw, and be within the relevant noise level for the area being served.

### B.	All grilles shall be provided with an aluminum opposed blade multi leaf damper, with loose key to allow adjustment of the concealed adjuster from the face of the grille. One loose key for every 20 grilles shall be provided.

### C.	Each supply grille shall have two sets of individually adjustable aluminum blades, one set horizontal the other vertical.

### D.	Extract grilles shall be as indicated on the drawings, and in the schedules. Where the grilles does not have to be matched to the supply grille, it shall be of the eggcrate type.

### E.	Non vision grilles be as indicated on the drawings and shall be of the inverted chevron type comprising a non-vision insert core held firmly between two mating flanged frames. In the case of door mounted applications these shall be rattleproof, provided with screw fixings and telescopic aluminum frames.

### F.	All grilles shall be supplied with a stove enamel paint finish to a BS RAL colour.

## 2.02	DIFFUSERS

### A.	Air diffusers shall be supplied and installed in accordance with the duties, sizes and locations shown on the drawings.

### B.	Square diffusers for supply air shall be manufactured from extruded aluminum and shall be supplied complete with opposed blade volume control dampers. Both dampers and grilles shall have concealed screw type fixings. Spring clip fixings shall not be permitted.

### C.	Where a supply diffuser is directly  connected to a stub duct which has a straight of less than two diameters or equivalent diameters, then an equalizing grid or deflector shall be used.

### D.	The frames of all diffusers shall be provided with positive seals with the except of those mounted on exposed ductwork. Frames shall be of a type compatible with the ceiling type or wall finish.

### E.	All diffusers shall be supplied with a stove enamel paint finish to a BS RAL colour as approved by the Architect.

### F.	All diffusers shall be provided with galvanized steel plenum boxes, lined with acoustic insulation. The plenums shall be sized to match the diffuser and be complete with fixing lugs and incorporate an opposed blade central damper adjustable from the diffuser face and it shall be sized to restrict the re-generated noise level.

### G.	The schedules provided indicate volume flows, throws, maximum noise levels and the Contractor shall ensure that the grille and diffuser manufacturer shall assess the data and confirms that his selections comply with the stated parameters.

## 2.03	LOUVERS

### A.	Air intakes and discharges associated with package units and fan convectors shall consist of ducted connections made to flanged openings formed in the galvanised sheet steel blanking plates fixed to the rear of the building weather louvres.  The blanking plates shall be used to cover over un-used areas of the weather louvres, and shall be provided under Division 15.

### B.	Louvers shall be made of heavy gauge extruded anodized finish aluminum bars.

# PART 3 EXECUTION

## 3.01	STORAGE

### A.	All air terminal devices shall be stored within a well lit container on purpose made shelving. The devices shall be stored in their original packaging to prevent damage to the finish.

## 3.02	GENERAL INSTALLATION

### A.	The air terminal devices shall be identified by reference number as to their final location. Plenum boxes shall be similarly numbered to reduce the risk of incorrect matching.

### B.	Grilles, diffusers and plenum boxes shall be supported independently from the building structure unless otherwise instructed by the Engineer.  Grilles diffusers and plenums shall not be supported from the ceiling grid.

### C.	All volume control dampers shall be left in the fully open position.

### D.	Diffusers shall be securely fixed to plenum boxes by means of concealed adjustable mounting brackets.

### E.	During construction the Contractor shall ensure that the location and fixing of all grilles and diffusers is fully coordinated between the relevant trades.

END OF SECTION 15940

| DIVISION – 15 MECHANICAL SECTION – 15996 | TECHNICAL SPECIFICATION MECHANICAL WORK ### HVAC TESTING, ADJUSTING, AND BALANCING |
| --- | --- |

PART 1 - GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes Testing, Adjusting and Balancing (TAB) to produce design objectives for the following:

      - Air Systems:

        - Constant-volume air systems.

      - Motors.

      - Temperature Measurements.

      - Vibration measuring.

      - Sound level measuring.

      - Indoor-air quality measuring.

      - Verifying that automatic control devices are functioning properly.

      - Reporting results of activities and procedures specified in this Section.

  - REFERENCES

    - Associated Air Balance Council:

      - AABC MN-1 - National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning System.

    - American Society of Heating, Refrigerating and Air-Conditioning Engineers:

      - ASHRAE 111 - Practices for Measurement, Testing, Adjusting and Balancing of Building Heating, Ventilation, Air-Conditioning and Refrigeration Systems.

    - Natural Environmental Balancing Bureau:

      - NEBB  -  Procedural  Standards  for  Testing,  Adjusting,  and  Balancing  of  Environmental Systems

  - DEFINITIONS

    - Adjust:  To regulate fluid flow rate and air patterns at the terminal equipment, such as to reduce fan speed or adjust a damper.

    - Balance:   To proportion flows within the distribution system, including submains, branches, and terminals, according to indicated quantities.

    - Barrier or Boundary: Construction, either vertical or horizontal, such as walls, floors, and ceilings that are designed and constructed to restrict the movement of airflow, smoke, odors, and other pollutants.

    - Draft: A current of air, when referring to localized effect caused by one or more factors of high air velocity, low ambient temperature, or direction of airflow, whereby more heat is withdrawn from a person's skin than is normally dissipated.

    - NC:  Noise criteria.

    - Procedure: An approach to and execution of a sequence of work operations to yield repeatable results.

    - RC:  Room criteria.

    - Report Forms: Test data sheets for recording test data in logical order.

    - Stair Pressurization System: A type of smoke-control system that is intended to positively pressurize stair towers with outdoor air by using fans to keep smoke from contaminating the stair towers during an alarm condition.

- Static Head: The pressure due to the weight of the fluid above the point of measurement. In a closed system, static head is equal on both sides of the pump.

- Suction Head: The height of fluid surface above the centerline of the pump on the suction side.

- System Effect: A phenomenon that can create undesired or unpredicted conditions that cause reduced capacities in all or part of a system.

- System Effect Factors: Allowances used to calculate a reduction of the performance ratings of a fan when installed under conditions different from those presented when the fan was performance tested.

- TAB:  Testing, adjusting, and balancing.

- Terminal: A point where the controlled medium, such as fluid or energy, enters or leaves the distribution system.

- Test:  A procedure to determine quantitative performance of systems or equipment.

- Testing, Adjusting, and Balancing (TAB) Firm: The entity responsible for performing and reporting TAB procedures.

  - SUBMITTALS

    - Qualification Data: Within 45 days from Contractor's Notice to Proceed, submit 4 copies of evidence that TAB firm and this Project's TAB team members meet the qualifications specified in "Quality Assurance" Article.

    - Certified TAB Reports: Submit two copies of reports prepared, as specified in this Section, on approved forms certified by TAB firm.

    - Sample Report Forms:  Submit two sets of sample TAB report forms.

    - Warranties specified in this Section.

  - QUALITY ASSURANCE

    - TAB Firm Qualifications: Engage a TAB firm certified by AABC or NEBB.

    - Certification of TAB Reports: Certify TAB field data reports. This certification includes the following:

      - Review field data reports to validate accuracy of data and to prepare certified TAB reports.

      - Certify that TAB team complied with approved TAB plan and the procedures specified and referenced in this Specification.

    - TAB Report Forms: Use standard forms from AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems" or NEBB “National Environmental Balancing Bureau”.

    - Instrumentation Type, Quantity, and Accuracy: As described in AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems.

    - Instrumentation Calibration: Calibrate instruments at least every six months or more frequently if required by instrument manufacturer.

      - Keep an updated record of instrument calibration that indicates date of calibration and the name of party performing instrument calibration.

  - PROJECT CONDITIONS

    - Full Owner Occupancy:  Owner will occupy the site and existing building during entire TAB period.

Cooperate with Owner during TAB operations to minimize conflicts with Owner's operations.

    - Partial Owner Occupancy: Owner may occupy completed areas of building before Substantial Completion. Cooperate with Owner during TAB operations to minimize conflicts with Owner's operations.

  - COORDINATION

    - Coordinate the efforts of factory-authorized service representatives for systems and  equipment, HVAC controls installers, and other mechanics to operate HVAC systems and equipment to support and assist TAB activities.

    - Notice:  Provide seven days' advance notice for each test.  Include scheduled test dates and times.

    - Perform TAB after leakage and pressure tests on air and water distribution systems have been satisfactorily completed.

  - WARRANTY

    - National Project Performance Guarantee: Provide a guarantee on AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems" forms or NEBB’s forms stating that a certified agent has tested and balanced (TAB) the systems to optimum performance capabilities according to the Contract Documents.

    - General Warranty: The National Project Performance guarantee specified in this Article shall not deprive the Owner of other rights the Owner may have under other provisions of the Contracts Documents and shall be in addition to, and run concurrent with, other warranties made by the Contractor under requirements of the contract Documents.

PART 2 - PRODUCTS (Not Applicable) PART 3 - EXECUTION

  - EXAMINATION

    - Examine the Contract Documents to become familiar with Project requirements and to discover conditions in systems' designs that may preclude proper TAB of systems and equipment.

      - Contract Documents are defined in the General and Supplementary Conditions of Contract.

      - Verify that balancing devices, such as test ports, gage cocks, thermometer wells, flow-control devices, balancing valves and fittings, and manual volume dampers, are required by the Contract Documents. Verify that quantities and locations of these balancing devices are accessible and appropriate for effective balancing and for efficient system and equipment operation.

    - Examine approved submittal data of HVAC systems and equipment.

    - Examine Project Record Documents described in Division 1 Section "Project Record Documents."

    - Examine design data, including HVAC system descriptions, statements of design assumptions for environmental conditions and systems' output, and statements of philosophies and assumptions about HVAC system and equipment controls.

    - Examine equipment performance data including fan and pump curves. Relate performance data to Project conditions and requirements, including system effects that can create undesired or unpredicted conditions that cause reduced capacities in all or part of a system.

    - Examine system and equipment installations to verify that they are complete and that testing, cleaning, adjusting, and commissioning specified in individual Sections have been performed.

    - Examine system and equipment test reports.

    - Examine HVAC system and equipment installations to verify that indicated balancing devices, such as test ports, gage cocks, thermometer wells, flow-control devices, balancing valves and fittings, and manual volume dampers, are properly installed, and that their locations are accessible and appropriate for effective balancing and for efficient system and equipment operation.

    - Examine systems for functional deficiencies that cannot be corrected by adjusting and balancing.

- Examine HVAC equipment to ensure that clean filters have been installed, bearings are greased, belts are aligned and tight, and equipment with functioning controls is ready for operation.

- Examine terminal units, such as variable-air-volume boxes, to verify that they are accessible and their controls are connected and functioning.

- Examine plenum ceilings used for supply air to verify that they are airtight. Verify that pipe penetrations and other holes are sealed.

- Examine strainers for clean screens and proper perforations.

- Examine three-way valves for proper installation for their intended function of diverting or mixing fluid flows.

- Examine heat-transfer coils for correct piping connections and for clean and straight fins.

- Examine system pumps to ensure absence of entrained air in the suction piping.

- Examine equipment for installation and for properly operating safety interlocks and controls.

- Examine automatic temperature system components to verify the following:

  - Dampers, valves, and other controlled devices are operated by the intended controller.

  - Dampers and valves are in the position indicated by the controller.

  - Integrity of valves and dampers for free and full operation and for tightness of fully closed and fully open positions. This includes dampers in multi zone units, mixing boxes, and variable- air-volume terminals.

  - Automatic modulating and shutoff valves, including two-way valves and three-way mixing and diverting valves, are properly connected.

  - Thermostats and humidistats are located to avoid adverse effects of sunlight, drafts, and cold

walls.

  - Sensors are located to sense only the intended conditions.

  - Sequence of operation for control modes is according to the Contract Documents.

  - Controller set points are set at indicated values.

  - Interlocked systems are operating.

  - Changeover from heating to cooling mode occurs according to indicated values.

- Report deficiencies discovered before and during performance of TAB procedures. Observe and record system reactions to changes in conditions. Record default set points if different from indicated values.

  - PREPARATION

    - Prepare a TAB plan that includes strategies and step-by-step procedures.

    - Complete system readiness checks and prepare system readiness reports.  Verify the following:

      - Permanent electrical power wiring is complete.

      - Hydronic systems are filled, clean, and free of air.

      - Automatic temperature-control systems are operational.

      - Equipment and duct access doors are securely closed.

      - Balance, smoke, and fire dampers are open.

      - Isolating and balancing valves are open and control valves are operational.

      - Ceilings are installed in critical areas where air-pattern adjustments are required and access to balancing devices is provided.

      - Windows and doors can be closed so indicated conditions for system operations can be met.

  - GENERAL PROCEDURES FOR TESTING AND BALANCING

    - Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems" or NEBB, SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing" and this Section.

    - Cut insulation, ducts, pipes, and equipment cabinets for installation of test probes to the minimum extent necessary to allow adequate performance of procedures. After testing and balancing, close probe holes and patch insulation with new materials identical to those removed. Restore vapor barrier and finish according to insulation Specifications for this Project.

    - Mark equipment and balancing device settings with paint or other suitable, permanent identification material, including damper-control positions, valve position indicators, fan-speed-control levers, and similar controls and devices, to show final settings.

    - Take and report testing and balancing measurements.

  - GENERAL PROCEDURES FOR BALANCING AIR SYSTEMS

    - Prepare test reports for both fans and outlets. Obtain manufacturer's outlet factors and recommended testing procedures.  Crosscheck the summation of required outlet volumes with required fan volumes.

    - Prepare schematic diagrams of systems' "as-built" duct layouts.

    - For variable-air-volume systems, develop a plan to simulate diversity.

    - Determine the best locations in main and branch ducts for accurate duct airflow measurements.

    - Check airflow patterns from the outside-air louvers and dampers and the return- and exhaust-air dampers, through the supply-fan discharge and mixing dampers.

    - Locate start-stop and disconnect switches, electrical interlocks, and motor starters.

    - Verify that motor starters are equipped with properly sized thermal protection.

    - Check dampers for proper position to achieve desired airflow path.

    - Check for airflow blockages.

- Check condensate drains for proper connections and functioning.

- Check for proper sealing of air-handling unit components.

- Check for proper sealing of air duct system.

  - PROCEDURES FOR CONSTANT-VOLUME AIR SYSTEMS

    - Adjust fans to deliver total indicated airflows within the maximum allowable fan speed listed by fan manufacturer.

      - Measure fan static pressures to determine actual static pressure as follows:

        - Measure outlet static pressure as far downstream from the fan as practicable and upstream from restrictions in ducts such as elbows and transitions.

        - Measure static pressure directly at the fan outlet or through the flexible connection.

        - Measure inlet static pressure of single-inlet fans in the inlet duct as near the fan as possible, upstream from flexible connection and downstream from duct restrictions.

        - Measure inlet static pressure of double-inlet fans through the wall of the plenum that houses the fan.

      - Measure static pressure across each component that makes up an air-handling unit, rooftop unit, and other air-handling and -treating equipment.

        - Simulate dirty filter operation and record the point at which maintenance personnel must change filters.

      - Measure static pressures entering and leaving other devices such as sound traps, heat recovery equipment, and air washers, under final balanced conditions.

      - Compare design data with installed conditions to determine variations in design static pressures versus actual static pressures. Compare actual system effect factors with calculated system effect factors to identify where variations occur. Recommend corrective action to align design and actual conditions.

      - Obtain approval from The Engineer for adjustment of fan speed higher or lower than indicated speed.   Make required adjustments to pulley sizes, motor sizes, and electrical connections to

accommodate fan-speed changes.

      - Do not make fan-speed adjustments that result in motor overload. Consult equipment manufacturers about fan-speed safety factors. Modulate dampers and measure fan-motor amperage to ensure that no overload will occur. Measure amperage in full cooling, full heating, economizer, and any other operating modes to determine the maximum required brake horsepower.

    - Adjust volume dampers for main duct, submain ducts, and major branch ducts to indicated airflows within specified tolerances.

      - Measure static pressure at a point downstream from the balancing damper and adjust volume dampers until the proper static pressure is achieved.

        - Where sufficient space in submain and branch ducts is unavailable for Pitot-tube traverse measurements, measure airflow at terminal outlets and inlets and calculate the total airflow for that zone.

      - Remeasure each submain and branch duct after all have been adjusted. Continue to adjust submain and branch ducts to indicated airflows within specified tolerances.

    - Measure terminal outlets and inlets without making adjustments.

      - Measure terminal outlets using a direct-reading  hood  or  outlet  manufacturer's  written instructions and calculating factors.

    - Adjust terminal outlets and inlets for each space to indicated airflows within specified tolerances of indicated values. Make adjustments using volume dampers rather than extractors and the dampers at air terminals.

      - Adjust each outlet in same room or space to within specified tolerances of indicated quantities without generating noise levels above the limitations prescribed by the Contract Documents.

      - Adjust patterns of adjustable outlets for proper distribution without drafts.

  - PROCEDURES FOR MOTORS

    - Motors, 1/2 HP and Larger: Test at final balanced conditions and record the following data:

      - Manufacturer, model, and serial numbers.

      - Motor horsepower rating.

      - Motor rpm.

      - Efficiency rating.

      - Nameplate and measured voltage, each phase.

      - Nameplate and measured amperage, each phase.

      - Starter thermal-protection-element rating.

    - Motors Driven by Variable-Frequency Controllers: Test for proper operation at speeds varying from minimum to maximum. Test the manual bypass for the controller to prove proper operation. Record observations, including controller manufacturer, model and serial numbers, and nameplate data.

  - PROCEDURES FOR TEMPERATURE MEASUREMENTS

    - During TAB, report the need for adjustment in temperature regulation within the automatic temperature-control system.

- Measure indoor wet- and dry-bulb temperatures every other hour for a period of two successive eight- hour days, in each separately controlled zone, to prove correctness of final temperature settings. Measure when the building or zone is occupied.

- Measure outside-air, wet- and dry-bulb temperatures.

  - PROCEDURES FOR VIBRATION MEASUREMENTS

    - Use a vibration meter meeting the following criteria:

      - Solid-state circuitry with a piezoelectric accelerometer.

      - Velocity range of 0.1 to 10 inches per second (2.5 to 254 mm/s).

      - Displacement range of 1 to 100 mils (0.0254 to 2.54 mm).

      - Frequency range of at least 0 to 1000 Hz.

      - Capable of filtering unwanted frequencies.

    - Calibrate the vibration meter before each day of testing.

      - Use a calibrator provided with the vibration meter.

      - Follow vibration meter and calibrator manufacturer's calibration procedures.

    - Perform vibration measurements when other building and outdoor vibration sources are at a minimum level and will not influence measurements of equipment being tested.

      - Turn off equipment in the building that might interfere with testing.

      - Clear the space of people.

    - Perform vibration measurements after air and water balancing and equipment testing is complete.

    - Clean equipment surfaces in contact with the vibration transducer.

    - Position the vibration transducer according to  manufacturer's  written  instructions  and  to  avoid interference with the operation of the equipment being tested.

    - Measure and record vibration on rotating equipment over 3 hp (2.2 kW).

    - Measure and record equipment vibration, bearing vibration, equipment base vibration, and building structure vibration. Record velocity and displacement readings in the horizontal, vertical, and axial planes.

      - Pumps:

        - Pump Bearing:  Drive end and opposite end.

        - Motor Bearing:  Drive end and opposite end.

        - Pump Base: Top and side.

        - Building:  Floor.

        - Piping:  To and from the pump after flexible connections.

      - Fans and HVAC Equipment with Fans:

        - Fan Bearing:  Drive end and opposite end.

        - Motor Bearing:  Drive end and opposite end.

        - Equipment Casing: Top and side.

        - Equipment Base:  Top and side.

        - Building:  Floor.

        - Ductwork: To and from equipment after flexible connections.

        - Piping:  To and from equipment after flexible connections.

      - Chillers and HVAC Equipment with Compressors:

        - Compressor Bearing:  Drive end and opposite end.

        - Motor Bearing:  Drive end and opposite end.

        - Equipment Casing: Top and side.

        - Equipment Base:  Top and side.

        - Building:  Floor.

        - Piping:  To and from equipment after flexible connections.

- For equipment with vibration isolation, take floor measurements with the vibration isolation blocked solid to the floor and with the vibration isolation floating.  Calculate and report the differences.

- Inspect, measure, and record vibration isolation.

  - Verify that vibration isolation is installed in the required locations.

  - Verify that installation is level and plumb.

  - Verify that isolators are properly anchored.

  - For spring isolators, measure the compressed spring height, the spring OD, and the travel-to- solid distance.

  - Measure the operating clearance between each inertia base and the floor or concrete base below.  Verify that there is unobstructed clearance between the bottom of the inertia base and the floor.

  - PROCEDURES FOR SOUND-LEVEL MEASUREMENTS

    - Perform  sound-pressure-level  measurements  with  an   octave-band   analyzer   complying   with ANSI S1.4 for Type 1 sound-level meters and ANSI S1.11 for octave-band filters.  Comply with requirements in ANSI S1.13, unless otherwise indicated.

    - Calibrate sound meters before each day of testing. Use a calibrator provided with the sound meter complying with ANSI S1.40 and that has NIST certification.

    - Use a microphone that is suitable for the type of sound levels measured. For areas where air velocities exceed 100 fpm (0.51 m/s), use a windscreen on the microphone.

    - Perform sound-level testing after air and water balancing and equipment testing are complete.

    - Close windows and doors to the space.

    - Perform measurements when the space is not occupied and when the occupant noise level from other spaces in the building and outside are at a minimum.

    - Clear the space of temporary sound sources so unrelated disturbances will not be measured. Position testing personnel during measurements to achieve a direct line-of-sight between the sound source and the sound-level meter.

    - Take sound measurements at a height approximately 48 inches (1200 mm) above the floor and at least

36  inches  (900  mm)  from  a  wall,  column,  and  other  large  surface  capable  of  altering  the measurements.

    - Take sound measurements in dBA and in each of the 8 unweighted octave bands in the frequency range of 63 to 8000 Hz.

    - Take sound measurements with the HVAC systems off to establish the background sound levels and take sound measurements with the HVAC systems operating.

  - Calculate the difference between measurements.  Apply a correction factor depending on the difference and adjust measurements.

- Perform sound testing at several locations on Project for each of the following space types. For each space type tested, select a measurement location that has the greatest sound level. If testing multiple locations for each space type, select at least one location that is near and at least one location that is remote from the predominant sound source.

  - Private office.

  - Open office area.

  - Conference room.

  - Auditorium/large meeting room/lecture hall.

  - Classroom/training room.

  - Patient room/exam room.

  - Sound or vibration sensitive laboratory.

  - Hotel room/apartment.

  - Each space with a noise criterion of RC or NC 25 or lower.

  - Each space with an indicated noise criterion of RC or NC 35 and lower that is adjacent to a mechanical equipment room or roof mounted equipment.

  - Inside each mechanical equipment room.

  - PROCEDURES FOR INDOOR-AIR QUALITY MEASUREMENTS

    - After air balancing is complete and with HVAC systems operating at indicated conditions, perform indoor-air quality testing.

    - Observe and record the following conditions for each HVAC system:

      - The distance between the outside-air intake and the closest exhaust fan discharge, cooling tower, flue termination, or vent termination.

      - Specified filters are installed.  Check for leakage around filters.

      - Cooling coil drain pans have a positive slope to drain.

      - Cooling coil condensate drain trap maintains an air seal.

      - Evidence of water damage.

      - Insulation in contact with the supply, return, and outside air is dry and clean.

    - Measure and record  indoor  conditions served  by each  HVAC system. Make measurements at multiple locations served by the system if required to satisfy the following:

      - Most remote area.

      - One location per floor.

      - One location for every 5000 sq. ft. (500 sq. m).

    - Measure and record the following indoor conditions for each location two times at two-hour intervals, and in accordance with ASHRAE 113:

      - Temperature.

      - Relative humidity.

      - Air velocity.

      - Concentration of carbon dioxide (ppm).

      - Concentration of carbon monoxide (ppm).

      - Nitrogen oxides (ppm).

      - Formaldehyde (ppm).

  - TEMPERATURE-CONTROL VERIFICATION

    - Verify that controllers are calibrated and commissioned.

    - Check transmitter and controller locations and note conditions that would adversely affect control functions.

    - Record controller settings and note variances between set points and actual measurements.

    - Check the operation of limiting controllers (i.e., high- and low-temperature controllers).

.E.	Check free travel and proper operation of control devices such as damper and valve operators.

- Check the sequence of operation of control devices.   Note air pressures and device positions and correlate with airflow and water flow measurements.  Note the speed of response to input changes.

- Check the interaction of electrically operated switch transducers.

- Check the interaction of interlock and lockout systems.

- Check main control supply-air pressure and observe compressor and dryer operations.

- Record voltages of power supply and controller output.  Determine whether the system operates on a grounded or non-grounded power supply.

- Note operation of electric actuators using spring return for proper fail-safe operations.

  - TOLERANCES

    - Set HVAC system airflow and water flow rates within the following tolerances:

      - Supply, Return, and Exhaust Fans and Equipment with Fans:  Plus 5 to plus 10 percent.

      - Air Outlets and Inlets:  0 to minus 10 percent.

      - Heating-Water Flow Rate:  0 to minus 10 percent.

      - Cooling-Water Flow Rate:  0 to minus 5 percent.

  - REPORTING

    - Initial Construction-Phase Report: Based on examination of the Contract Documents as specified in "Examination" Article, prepare a report on the adequacy of design for systems' balancing devices. Recommend changes and additions to systems' balancing devices to facilitate proper performance measuring and balancing. Recommend changes  and  additions  to  HVAC  systems  and  general construction to allow access for performance measuring and balancing devices.

    - Status Reports:  As Work progresses, prepare reports to describe completed procedures, procedures in progress, and scheduled procedures. Include a list of deficiencies and problems found in systems being tested and balanced.  Prepare a separate report for each system and each building floor for systems serving multiple floors.

  - FINAL REPORT

    - General: Typewritten, or computer printout in letter-quality font, on standard bond paper, in three- ring binder, tabulated and divided into sections by tested and balanced systems.

    - Include a certification sheet in front of binder signed and sealed by the certified testing and balancing engineer.

      - Include a list of instruments used for procedures, along with proof of calibration.

    - Final Report Contents: In addition to certified field report data, include the following:

      - Pump curves.

      - Fan curves.

      - Manufacturers' test data.

      - Field test reports prepared by system and equipment installers.

      - Other information relative to equipment performance, but do not include Shop Drawings and Product Data.

    - Vibration Measurement Reports:

      - Date and time of test.

      - Vibration meter manufacturer, model number, and serial number.

      - Equipment designation, location, equipment, speed, motor speed, and motor horsepower.

      - Diagram of equipment showing the vibration measurement locations.

      - Measurement readings for each measurement location.

      - Calculate isolator efficiency using measurements taken.

      - Description of predominant vibration source.

    - Sound Measurement Reports: Record sound measurements on octave band and dBA test forms and on an NC or RC chart indicating the decibel level measured in each frequency band for both "background" and "HVAC system operating" readings. Record each tested location on a separate NC or RC chart.  Record the following on the forms:

      - Date and time of test.  Record each tested location on its own NC curve.

      - Sound meter manufacturer, model number, and serial number.

      - Space location within the building including floor level and room number.

      - Diagram or color photograph of the space showing the measurement location.

      - Time weighting of measurements, either fast or slow.

      - Description of the measured sound:  steady, transient, or tonal.

      - Description of predominant sound source.

    - Indoor-Air Quality Measurement Reports for Each HVAC System:

      - HVAC system designation.

      - Date and time of test.

      - Outdoor temperature, relative humidity, wind speed, and wind direction at start of test.

      - Room number or similar description for each location.

      - Measurements at each location.

      - Observed deficiencies.

    - Instrument Calibration Reports:

      - Report Data:

        - Instrument type and make.

        - Serial number.

        - Application.

        - Dates of use.

        - Dates of calibration.

  - INSPECTIONS

    - Initial Inspection:

      - After testing and balancing are complete, operate each system and randomly check measurements to verify that the system is operating according to the final test and balance readings documented in the Final Report.

      - Randomly check the following for each system:

| a. | Measure airflow of at least 10 percent of air outlets. |  |
| --- | --- | --- |
| b. | Measure water flow of at least 5 percent of terminals. |  |
| c. | Measure room temperature at each thermostat/temperature sensor. |  |
|  | Compare the reading to the set point. |  |
| d. | Measure sound levels at two locations. |  |
| e. | Measure space pressure of at least 10 percent of locations. |  |
| f. | Verify that balancing devices are marked with final balance position. |  |
| g. | Note deviations to the Contract Documents in the Final Report. |  |

    - Final Inspection:

      - After initial inspection is complete and evidence by random checks verifies that testing and balancing are complete and accurately documented in the final report, request that a final inspection be made by the Engineer.

      - TAB firm  test and  balance engineer  shall  conduct  the inspection in  the presence of  the

Engineer.

      - The Engineer shall randomly select measurements documented in the final report to be rechecked.  The rechecking shall be limited to either 10 percent of the total measurements recorded, or the extent of measurements that can be accomplished in a normal 8-hour business day.

      - If the rechecks yield measurements that differ from the measurements documented in the final report by more than the tolerances allowed, the measurements shall be noted as "FAILED."

      - If the number of "FAILED" measurements is greater than 10 percent of the total measurements checked during the final inspection, the testing and balancing shall be considered incomplete and shall be rejected.

      - TAB firm shall recheck all measurements and make adjustments.  Revise the final report and

balancing device settings to include all changes and resubmit the final report.

      - Request a second final inspection. If the second final inspection also fails, Owner shall contract the services of another TAB firm to complete the testing and balancing in accordance with the Contract Documents and deduct the cost of the services from the final payment.

  - ADDITIONAL TESTS

    - Within 90 days of completing TAB, perform additional testing and balancing to verify that balanced conditions are being maintained throughout and to correct unusual conditions.

    - Seasonal Periods: If initial TAB procedures were not performed during near-peak summer and winter conditions, perform additional testing, inspecting, and adjusting during near-peak summer and winter conditions.

END OF SECTION 15996

المواصفات الفنية لأثاث المختبرات

شروط عامة

على الجهة المنفذة التأكد من القياسات والأبعاد على الواقع قبل البدء بالأعمال. كما عليها تنسيق الأعمال مع جميع المقاولين الفرعيين بالموقع خلال تنفيذ المشروع.

على الجهة المنفذة لأثاث المختبرات وأجهزة شفط الغازات تقديم مخططات تنفيذية تشمل القياسات ومواصفات المواد لطاولات وخزائن المختبر.

على الجهة المنفذة الحصول على الموافقة الخطية على المواد ومواصفات الأعمال من جهة الإشراف قبل البدء بأية أعمال.

يجب على الجهة المنفذة تقديم كافة التفاصيل والعينات لجميع الأعمال التي سيتم تنفيذها ليتم الموافقة عليها من قبل جهة الإشراف قبل البدء بتصنيعها و توريدها، على أن تتطابق المواد الموردة للموقع والأعمال المنفذة لاحقا مع العينات والنماذج التي تمت الموافقة عليها. ويحق للمهندس المشرف زيارة الشركة الصانعة خلال أعمال التصنيع للتأكد من نوعية وجودة المواد المستخدمة.

يجب على الجهة المنفذة إصدار رسومات تنفيذية تفصيلية حيثما يلزم وحسب تعليمات جهة الإشراف ، كما يجب تقديم مواصفات فنية بكافة القطع والأجزاء المستخدمة بالمختبر بغرض اعتمادها من الجهة المسؤولة.

يتم تركيب جميع أجزاء الطاولات وأعمال الإنهاء خارج موقع العمل لدى شركه معتمدة وذات خبرة بهذا المجال ما عدا بعض الأعمال التي تحتاج إلى تثبيتها في الموقع ويتم تزويد جهة الإشراف بشهادة من الشركة الصانعة على أساس ذلك.

يجب أن يقوم بتنفيذ الأعمال عمال وحرفيون مدربين ذو مهارة وخبره في تنفيذ هذا النوع من الأعمال كما يجب أن يكون مشرف الموقع على دراية تامة بنوع الأعمال المطلوبة والمواصفات الفنية وبوثائق العقد.

يجب أن تكون الهياكل المعدنية قوية وقادرة على حمل سطح العمل والخزائن، كما يجب أن تكون  الخزائن قابله للاستبدال، الفك، أو التركيب.

يجب على المقاول أن يقوم بتوريد وتركيب محابس أمان للماء والغاز اسفل الطاولات ليتم شبكها مع حنفيات المختبرات بحيث تزود كل طاولة عمل وداخل خزانة الخدمات الملحقة بها بمحابس امان للماء والغاز.

الهيكل المعدني:

يتكون الهيكل المعدني للنظام المحمول من تيوب معدني مربع قياس 30×30×1.5 ملم مزود بأرجل قابلة للرفع والتنزيل بمسافة  ±15mm لتعديل الطاولة عندما تكون الأرض غير مستوية.

يتم تثبيت الطاولات بالأرض بعد معايرتها بواسطة قواعد وبراغي مصنوعة من معدن غير قابل للصدأ.

طريقة لحام الجوانب بواسطة ثاني أكسيد الكربون أو الارجون.

جميع الأجزاء المعدنية يجب أن تغسل من الزيوت والصدأ وتعالج معالجة كيماوية ثم تطلى حراريا  ببودرة الابيوكسي ذات المقاومة العالية للمواد الكيماوية.

أسطــــــح العمــــــــل:

يجب أن تكون زوايا وأحرف أسطح العمل مبرومة ويجب أن يتم توصيل قطع الأوجه بواسطة معجونة الايبوكسي جزئين، كما يتم تزويد بانيل على الحائط من نفس المادة.

كما يجب أن يكون الوجه من الأسفل مزودة بفرزة عمق 3 ملم وعرض 3 ملم تقريبا لمنع انزلاق السوائل اسفل الوجه.

على ان تكون اسطح العمل كما هو موضح ادناه :

مختبر الكيمياء/الأحياء:  يجب أن تكون من الجرانيت المحلي سماكة 3 سم . كما يجب أن يكون سطح العمل لأحواض الطلاب مزود بحفة مرتفعة (Marine Edge) لمنع انسكاب السوائل خارج منطقة الحوض.

احواض المختبرات :

يجب ان تكون جميع الاحواض من مادة الستينلس ستييل المقاوم للأحماض ويتم تركيب جميع الاحواض ( في مختبرات الفيزياء والكيمياء ) بمستوى سطح العمل بحيث لا يكون هنالك عائق للسوائل في محيط الحوض ، ويجب تزويد كل حوض بسيفون BOTTLE من مادة البولي بروبيلين الخاصة بالمختبرات لون اسود وشبكها مع شبكة التصريف الصحي وايضا تزويد كل حوض بالبرابيش المرنة وجميع القطع لشبكها بشبكة المياه وكذلك السلسلة والسدادة الكاوتشوك .

الخزائن:

يجب أن تكون مصنوعة من الخشب المعاكس سماكة 18 ملم على الأقل مكبوس حراريا على الجهتين بالفورمايكا سماكة 0.7 ملم لون أبيض أو بيج مع حرف PVC بنفس لون بالفورمايكا سماكة 0.5 ملم يثبت بواسطة لاصق حراري على درجة 200 درجة مئوية.

الظهر مصنوع من    MDF سماكة 5  ملم بنفس لون الفورمايكا.

ظهر خزانة الحوض من المعاكس سماكة 12ملم على الأقل.

الأرفف من الخشب المعاكس سماكة 18 ملم على الأقل مكبوس حراريا على الجهتين بالفورمايكا سماكة 0.7 ملم لون أبيض أو بيج مع حرف PVC بنفس لون لالفورمايكا سماكة 0.5 ملم من أربع جهات وقابلة للرفع والتنزيل بمسافات متساوية لا تزيد عن 35سم.

سطح الخزائن من الجرانيت المحلي

الأبواب وأوجه الجوارير:

من المعاكس سماكة 18 ملم مغطى بالفورمايكا سطحها خشن سماكة 0.9 ملم على الأقل على الوجهين والأحرف من الـ PVC سماكة 3 ملم على حسب الألوان التي يعتمدها المهندس المشرف المقترحة ويتم تثبيت الأحرف بواسطة آلات أتوماتيكية و لاصق حبيبي حراري على درجة 200 مئوية. درف الخشب التي تتضمن زجاج لخزائن العينات والتخزين يجب أن يتم تثبيت الزجاج سماكة 5 ملم (سيكوريت) كحد ادنى بواسطة بروفيل بلاستيك بعد عمل الفتحة اللازمة بالدرفة الخشب كما تشتمل الدرفة على جريل تهوية من الألمنيوم أو البلاستيك حسب ما هو موضح في الرسم .

ابواب خزائن العرض من الزجاج سماكة 5 ملم على الاقل ، سحاب محمولة على عجلات معدنية من الستانلس ستيل  وأرفف زجاج قابله للتعديل ومزوده باناره علوية مخفيه ضمن بانيل علوي.

التسكيرات الامامية والجانبية والجلوس

يجب أن تكون مصنوعة من الخشب المعاكس سماكة 12 ملم على الأقل مكبوس حراريا على الجهتين بالفورمايكا سماكة 0.7 ملم لون أبيض أو بيج مع أحرف PVC بنفس لون لالفورمايكا سماكة 0.5 ملم على جميع الجهات يثبت بواسطة لاصق حراري على درجة 200 درجة مئوية.

وأن تكون قابلة للفك والتثبيت بواسطة حمالات وبراغي قطر 6ملم كي يتم الوصول إلى مناطق الخدمات بسهولة.

الاكسسوارات:

الفصالات يجب أن تكون قابلة للتعديل (المعايرة) 3 جهات بواسطة براغي تعديل قابلة للفتح 180 درجة على الأقل، مطلية بالنيكل، يجب أن تكون الفصاله قابله للتركيب بدون استخدام أي عدد يدويه .

كافة  الجوارير مصنوعة من الحديد المطلي ببودرة الايبوكسي تسير على عجلات بلاستيك وتثبت على جوانب الخزانة، يجب أن يكون قاع الجوارير مصنوع من نفس المعدن ومعالج بنفس الطريقة سماكة 12 ملم على الأقل ولها القدرة على تحمل وزن 30 كجم على الأقل.

الأبواب والجوارير يتم تزويدها بمسكة على عرض الباب أو الجارور من البلاستيك الصلب أوالالمنيوم الصلب المطلي بالايبوكسي والمسكات حسب الألوان المعتمدة.

يتم استعمال براغي وخردوات من النوع الممتاز ويجب تقديم عينات للمهندس المشرف على الموقع لاعتمادها.

زجاج السحاب سماكة 5ملم على الأقل مزود بسكة سفلية وعلوية من الألمنيوم مع عجلات معدنية تسير على فرزة سفلية.

يجب تزويد الخزائن والجوارير بأقفال (كما هو موضح بالرسم ) بحيث يكون القفل من النوع الممتاز والسلندر قطر 18ملم على الأقل مع مفتاح سويتش (عدد 2) لكل قفل.

الخشب والفورمايكا:

يجب ان يكون الخشب المعاكس يجب أن يكون نخب والفورمايكا نخب اول مصنعة حسب المواصفات الأوروبية أو الأمريكية.

الحنفيـات والمخـارج والمرشــات اليدويــة:

يجب أن تكون صناعة شركة معتمدة دولياً ويجب تمييز لون المسكة حسب نوع استخدامها ( الماء أو الغاز ) بناء على المواصفات الأوروبية ومصنعة من افضل أنواع النحاس ومعالج بطبقة نهائية من البوليستر لكر- دهان بودرة حراري.

- حنفيات الغاز  يجب أن تكون مزودة بمقبض حماية لا يعمل إلا عند رفع المقبض ثم إدارته وأن تكون كافة الحنفيات مزوده بفوهة دقيقه لوصلها بأي خرطوم خدمات.

- دوش الطوارئ يجب أن يتوفر به صمام داخلي للتحكم بضغط المياه وان تكون الأجزاء المعدنية والمواسير مصنوعة من النحاس المطلي بمواد مقاومة للأحماض باللون أحمر وتعمل على ضغط لا يقل عن 1 بار كما ويجب ان يكون ذو بنية قوية ، ويتم تشغيله عن طريق عتلة يتم سحبها الى الاسفل .

- المرشات الخاصة بالعين مزودة بحوض من الستينلس ستيل وأكواب مطاطية لحماية العين عند الاستعمال مع غطاء مانع للغبار.

أباريــز الكهربـــــــاء:

يجب أن تكون الأباريز من النوع الثلاثي نظام إنجليزي مزود بمفتاح ON/OFF وحسب ما يعتمدها المهندس المشرف. يتم تثبيتها بشكل مناسب.

لوحة تنشيف الزجاجيات:

يجب أن تكون مصنوعة من مواد مقاومة للماء مع صينية لتجميع المياه مصبوبة مع اللوحة كقطعة واحدة ومصرف يربط مع الحوض والحمالات مصنوعة من مادة بولستايرين ومزوده بـ 64 إصبع تعليق للزجاجيات (حمالة) على الأقل، كما ويجب أن يتم تزويد لوح تنشيف الزجاجيات بمصرف لتصريف المياه الزائدة.

طول الحمالات 10-15سم.

قياس اللوحة 45×60 سم .

ملاحظات عامة :

ضرورة اخذ تمديدات الماء والغاز والصرف الصحي والكهرباء بعين الاعتبار اثناء وضع البنية التحتية للمختبرات .

أجهـــزة طـرد الأبخــــــرة:

عام: يجب أن بكون الجهاز مصنوع بمواصفات فنية عالية وعالمية ويجب أن يتم فحصه قبل التركيب وبعده .

القياس:

العرض : 120 سم

العمق:   90 سم

الإرتفاع: 240 سم

الحجرة العلوية:

يجب أن تكون مصنوعة من مادة مقاومة للماء والرطوبة والحرارة والغازات بسماكة لا تقل عن 18 ملم من ألواح الخشب المعاكس ملبسة حرارياً بالفورمايكا لون ابيض من الداخل سماكة 0.7 ملم على الاقل ومن الخارج يتم تلبيس الحجرة بالفورمايكا الخشنة سماكة 0.9 ملم لون ابيض  او حسب رأي المهندس المشرف.

ويجب أن تكون جميع الأحرف ملبسة ببروفيل بلاستيك أو ألمنيوم. وأن تكون جوانب الجهاز الظاهرة مزودة بنوافذ زجاجية ذات سماكة لا تقل عن 10ملم من زجاج السيكوريت المقوى ، وان يتم تثبيتها بواسطة بروفيل بلاستيك خاص من قطعتين داخلية وخارجية والزجاج محشور بينهما.

الفواصل الداخلية:

يجب أن تكون مصنوعة من مادة مقاومة للماء والرطوبة والحرارة والغازات نوع Trespa او ما يعادلها بسماكة لا تقل عن 6 ملم من الواح صلبة ناتجة عن الضغط العالي تحت درجة عالية جدا على خشب معاكس سماكة 18 ملم تقريباً ، ومصممة بطريقة تسمح بتوزيع الهواء على ارتفاع الحجرة .

سطح العمل :

يجب ان يكون سطح العمل في جهاز شفط الغازات مصنوع من مادة الايبوكسي ( Epoxy Resin ) سماكة 2-3 سم ، لون اسود مع تجويف لمنع انزلاق السوائل على الاطراف .

الإنارة

يجب أن تكون الإنارة من ضوء نيون مزدوج مثبتة خارج الغرفة محكم الإغلاق من تسرب الغازات ويتم تثبيتها أعلى حجرة الغازات من الخارج.

الخدمات : يجب تزويد الجهاز ب :

حوض بيضاوي مصنوع من مادة الايبوكسي ، وسيفون مصنوع من مادة البوليبروبلين الخاصة بالمختبرات لون اسود بعمق (25سم) تقريباً ، وبقطر لا يقل عن 30 سم .

مخرج ماء ومخرج غاز يتم التحكم بهما من الخارج بواسطة محابس تثبت على لوحة الخدمات ، مصنوعة من مادة مقاومة للحموض والقواعد والغازات المنبعثة من المواد الكيماوية ، صنبور الماء ارتفاعه (25سم) تقريباً ، صنبور الغاز : مثبت على سطح منضدة العمل داخل الخزانة ارتفاعه لا يقل عن (15 سم ) يتصل بموقد لهب بنسن عن طريق انبوب بلاستيكي ويتصل من اسفل سطح العمل بمحبس امان ( داخل الخزانة السفلية ) .

ابريز كهرباءمزدوج بمفتاح ON/OFF .

مفتاح للانارة 5 امبير .

مفتاح للمروحة 15 امبير .

على ان يتم تثبيتها جميعاً على لوحة الخدمات الامامية للخزانة ، وحسب ما هو موضح بالشكل .

كما ويجب ان تكون جميع الخدمات والتوصيلات سهل الوصول اليها في حالة الصيانة وذات منشأ اوروبي .

كما ويجب تركيب علبة تجميع للكهرباء في اعلى الجهاز مع مفتاح رئيسي .

جميع وصلات الغاز يجب ان تكون مصنوعة من النحاس .

الزجاج:

يجب أن يكون سماكة 10 ملم على الاقل من الزجاج الشفاف والمقوى (سيكوريت).

ويجب أن تكون المسكة على طول الواجهة ، مطلي بالبودرة الإيبوكسي.

ويجب أن يكون الزجاج سهل الرفع والتنزيل ( يتحرك عمودياً ) بواسطة بكرات خاصة كل بكرة تتحمل 30 كجم على الأقل.

يمكن تثبيته اثناء رفعه عند أي مسافة مطلوبة بيسر وسهولة .

المروحة:

يجب أن تكون المروحة (Centrifugal) مصنوعة من البولي بروبيلين من النوع الخاص بالغازات والمقاوم لأشعة الشمس والعوامل الجوية فاز واحد قطر 200 ملم على الأقل.

ويجب أن يتم تثبيتها في مكان مناسب وشبكها مع الجهاز بواسطة مواسير وأكوع ومواسير مرنة من الـ Stainless steel قطر 20 سم على الأقل ( 8 انش) وتوصل في الموقع .

ترتفع انابيب تصريف الهواء عن اعلى نقطة في سطح المبنى بما لا يقل عن 2 متر وفي منطقة بعيدة عن مجرى الهواء الاعتيادي .

المروحة صناعة اوروبية او ما يعادلها .

قدرتها محسوبة بحيث تضمن سرعة دخول الهواء إلى الجهاز  بمقدار 0.5 – 0.7 متر بالثانية بعد التركيب وسرعة دوارنها (2700-3000) دورة / دقيقة تقريباً .

يتم فحص السرعة بواسطة جهاز فحص بعد التركيب للتأكد من تحقيقها للسرعة المطلوبة.

مخرج الجهاز الخاص بالهواء يجب أن يكون من الـ PVC ويثبت في أعلى الحجرة.

مجرى الهواء والاكواع والطربوش : تكون بعيدة عن نوافذ المبنى لدواعي السلامة العامة ، مع تزويد نهاية المجرى بصمام يفتح باتجاه واحد فقط ، ليمنع دخول مياه الامطار والابخرة المتصاعدة .

الخزانة السفلية:

جميع جدران وابواب ورفوف الخزانة السفلية مصنوعة من خشب المعاكس سمك 18 ملم مغطى بالفورمايكا لون ابيض من الداخل والخارج فيها رفان متحركان ويوجد بداخلها محبسي امان خاصين بالماء والغاز ومزودة بقفل ومفتاح ومقبض معدني مناسب وابوابها ( الدرفتين ) مزودتين بنوافذ تهوية مناسبة قطرها 10 سم تقريباً ، مغلقة من الخارج بغطاء بلاستيكي مقاوم لابخرة المواد الكيماوية . مع تلبيس القاعدة بالواح البوليبروبلين سماكة 4 ملم على الاقل .

تزويد حجرة العمل بمسرب للهواء ( Air Foil ) سفلي ، مصنوع من مادة الستانلس ستيل او من معدن لون اسود معالج ومدهون ببودرة الايبوكسي ومركب بحيث تنساب الابخرة والغازات بالشكل الصحيح الى الخارج .